## ZW5000 Series
[10 empty] | REV 4/8/24 | Zurn Water, LLC ¦ Wilkins 1747 Commerce Way, Paso Robles, CA 93446 USA
|  |  | Fire Valve sizing, Adjustable Outlet Pressure | [7 empty] | Ph. 855-663-9876 |  | ZURN.COM
For all 2-1/2" ZW5000 series valves, hose or sprinkler
1. Enter data in cells with green column headings | [5 empty] | *All calculated outlet pressures have a tolerance +/- 10%
2. Columns M, N, O, Q will fill out automatically | [5 empty] | *Outlet pressures must be below 175 PSI for conformance to UL listing
(Click tabs below for other models) | [10 empty] | NOTE: Outlet pressure values display RED if valve setting does not meet desired residual outlet pressure (column J) or if calculated static or residual outlet pressure exceed UL limit of 175 PSI
| 3. Place an "X" in desired body style | [29 empty] | Setting | Residual | [9 empty] | Outlet PSI | [9 empty] | Setting | Residual | [9 empty] | Outlet PSI | [14 empty] | Static | Outlet PSI
[6 empty] | Required Inputs | [24 empty] | Setting 0-5 | GLOBE |  | Setting 5-10 |  |  | Setting 10-15 |  |  |  |  | Setting 0-5 |  |  | Setting 5-10 |  |  | Setting 10-15 |  |  |  | Setting 0-5 | Angle |  | Setting 5-10 |  |  | Setting 10-15 |  |  |  |  | Setting 0-5 |  |  | Setting 5-10 |  |  | Setting 10-15 | [9 empty] | Setting 0-5 |  |  |  | Setting 5-10 |  |  |  | Setting 10-15
| Angle Body | Globe Body | Qty | Floor | Stair / Standpipe | Static Inlet (psi) | Residual Inlet (psi) | Flow (gpm) | Desired Residual Outlet Min (psi) | Desired Residual Outlet Max (psi) | Setting | Static Outlet | Residual Outlet | Model (Part Number) | Errors | Valid Model Choices | Description | Please select a body style | Static Inlet too Low | Static Inlet too High | Residual Inlet too Low | Residual Inlet too High | Flow too Low | Flow too High | Desired too Low | Desired higher than inlet | Angle Can't achieve desired residual | Globe Can't achieve desired residual | Select just one body style | Outlet exceeds max desired | Low Inlet | Medium Inlet | High Inlet | Low Inlet | Medium Inlet | High Inlet | Low Inlet | Medium Inlet | High Inlet | Raw setting | Setting rounded | Low Inlet | Medium Inlet | High Inlet | Low Inlet | Medium Inlet | High Inlet | Low Inlet | Medium Inlet | High Inlet | Outlet PSI | Low Inlet | Medium Inlet | High Inlet | Low Inlet | Medium Inlet | High Inlet | Low Inlet | Medium Inlet | High Inlet | Raw setting | Setting rounded | Low Inlet | Medium Inlet | High Inlet | Low Inlet | Medium Inlet | High Inlet | Low Inlet | Medium Inlet | High Inlet | Outlet PSI | Angle Setting | Angle Outlet | Globe Setting | Globe Outlet | Setting | Residual Outlet | Low Inlet | Medium Inlet | Med High Inlet | High Inlet | Low Inlet | Medium Inlet | Med High Inlet | High Inlet | Low Inlet | Medium Inlet | Med High Inlet | High Inlet | Outlet PSI | Angle Resid Out | Globe Resid Out
|  | X |  |  |  | 250 | 225 | 100 | 120 | 130 | 8 | 154 | 123 |  |  | Hose Valves | [14 empty] | 0 | 0 | 0 | 0 | 0 | 7.5829 | 0 | 0 | 0 | 7.5829 | 8 | 0 | 0 | 0 | 0 | 0 | 122.866 | 0 | 0 | 0 | 122.866 | 0 | 0 | 0 | 0 | 0 | 7.3883 | 0 | 0 | 0 | 7.3883 | 8 | 0 | 0 | 0 | 0 | 0 | 123.8557 | 0 | 0 | 0 | 123.8557 | 0 | 0 | 8 | 122.866 | 8 | 122.866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 154.0286 | 0 | 0 | 0 | 0 | 154.0286 | 123.8557 | 122.866 | 0.98972
[16 empty] | ZW5000G | 2-1/2" Pressure Reducing Hose valve, angle body, Grvd x NH(NST) | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | ZW5000GCC | 2-1/2" Pressure Reducing Hose valve, angle body, Grvd x NH(NST) w/cap chain | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | ZW5000 | 2-1/2" Pressure Reducing Hose valve, angle body, FNPT x NH(NST) | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | ZW5000CC | 2-1/2" Pressure Reducing Hose valve, angle body, FNPT x NH(NST) w/cap chain | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | ZW5000ILG | 2-1/2" Pressure Reducing Hose valve, inline body, Grvd x NH(NST) | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | ZW5000ILGCC | 2-1/2" Pressure Reducing Hose valve, inline body, Grvd x NH(NST) w/cap chain | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | ZW5000IL | 2-1/2" Pressure Reducing Hose valve, inline body, FNPT x NH(NST) | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | ZW5000ILCC | 2-1/2" Pressure Reducing Hose valve, inline body, FNPT x NH(NST) w/cap chain | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | ZW5000GST | 2-1/2" Pressure Reducing Hose valve, angle body, Grvd x Special Thread | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | ZW5000GSTCC | 2-1/2" Pressure Reducing Hose valve, angle body, Grvd x Special Thread w/cap chain | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | ZW5000ST | 2-1/2" Pressure Reducing Hose valve, angle body, FNPT x Special Thread | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | ZW5000STCC | 2-1/2" Pressure Reducing Hose valve, angle body, FNPT x Special Thread w/cap chain | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | ZW5000SF | 2-1/2" x 3" Pressure Reducing Hose valve, angle body, FNPT x NH(NST) | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | ZW5000SFCC | 2-1/2" x 3" Pressure Reducing Hose valve, angle body, FNPT x NH(NST) w/cap chain | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | ZW5000GCCCH | 2-1/2" Pressure Reducing Hose valve, angle body, Grvd x NH(NST) chrome w/cap chain | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | ZW5000CCCH | 2-1/2" Pressure Reducing Hose valve, angle body, FNPT x NH(NST) chrome w/cap chain | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | ZW5000ILGCCCH | 2-1/2" Pressure Reducing Hose valve, inline body, Grvd x NH(NST) chrome w/cap chain | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | ZW5000ILCCCH | 2-1/2" Pressure Reducing Hose valve, inline body, FNPT x NH(NST) chrome w/cap chain | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | ZW5000GSTCCCH | 2-1/2" Pressure Reducing Hose valve, angle body, Grvd x Special Thread chrome w/cap chain | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | ZW5000STCCCH | 2-1/2" Pressure Reducing Hose valve, angle body, FNPT x Special Thread chrome w/cap chain | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | ZW5000SFCCCH | 2-1/2" x 3" Pressure Reducing Hose valve, angle body, FNPT x NH(NST) chrome w/cap chain | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | Hose Rack Valves | [14 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | ZW5000F | 2-1/2" Pressure Reducing Hose rack valve, angle body, FNPT x FNPT | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | ZW5000FIL | 2-1/2" Pressure Reducing Hose rack valve, inline body, FNPT x FNPT | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | ZW5000FCH | 2-1/2" Pressure Reducing Hose rack valve, angle body, FNPT x FNPT chrome | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | ZW5000FILCH | 2-1/2" Pressure Reducing Hose rack valve, inline body, FNPT x FNPT chrome | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | Sprinkler Valves (includes supervisory switch) | [14 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | ZW5004G | 2-1/2" Pressure Reducing Sprinkler valve, angle body, Grvd x Grvd | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | ZW5004 | 2-1/2" Pressure Reducing Sprinkler valve, angle body, FNPT x FNPT | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | ZW5004ILG | 2-1/2" Pressure Reducing Sprinkler valve, inline body, Grvd x Grvd | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | ZW5004IL | 2-1/2" Pressure Reducing Sprinkler valve, inline body, FNPT x FNPT | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | ZW5004GCAP | 2-1/2" Pressure Reducing Sprinkler valve, angle body, Grvd x Grvd No hand wheel | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | ZW5004CAP | 2-1/2" Pressure Reducing Sprinkler valve, angle body, FNPT x FNPT No hand wheel | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | ZW5004ILGCAP | 2-1/2" Pressure Reducing Sprinkler valve, inline body, Grvd x Grvd No hand wheel | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[16 empty] | ZW5004ILCAP | 2-1/2" Pressure Reducing Sprinkler valve, inline body, FNPT x FNPT No hand wheel | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[31 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
ZW5000 static outlet pressure data
[31 empty] | Body | inlet pressure |  | setting range
[31 empty] | Style | min | max | min | max | K | L | M | N | P | Q
[31 empty] | All | 50 | 100 | 0 | 5 | 0.4 | 10 | 0.7 | 15 | 0 | 5
[31 empty] | All | 50 | 100 | 5 | 10 | 0.7 | 15 | 1 | 0 | 5 | 10
[31 empty] | All | 50 | 100 | 10 | 15.01 | 1 | 0 | 1 | 0 | 10 | 15
[31 empty] | All | 100 | 150 | 0 | 5 | 0.4 | 10 | 0.4 | 45 | 0 | 5
[31 empty] | All | 100 | 150 | 5 | 10 | 0.4 | 45 | 0.7 | 30 | 5 | 10
[31 empty] | All | 100 | 150 | 10 | 15.01 | 0.7 | 30 | 1 | 0 | 10 | 15
[31 empty] | All | 150 | 250 | 0 | 5 | 0.4 | 10 | 0.34759 | 52.861 | 0 | 5
[31 empty] | All | 150 | 250 | 5 | 10 | 0.34759 | 52.861 | 0.36 | 81 | 5 | 10
[31 empty] | All | 150 | 250 | 10 | 15.01 | 0.36 | 81 | 0.8 | 30 | 10 | 15
[31 empty] | All | 250 | 400 | 0 | 5 | 0.37654 | 15.8642 | 0.47619 | 9.5238 | 0 | 5
[31 empty] | All | 250 | 400 | 5 | 10 | 0.47619 | 9.5238 | 0.42667 | 64.3333 | 5 | 10
[31 empty] | All | 250 | 400 | 10 | 15.01 | 0.42667 | 64.3333 | 0.3 | 155 | 10 | 15
ZW5000 series residual pressure data
[31 empty] | Body | inlet pressure min: inlet pressure; setting range min: setting range
[31 empty] | Style | min | max | min | max | A | B | C | D | E | F | G | H | J
[31 empty] | Angle | 50 | 100 | -10 | 5 | -5.399e-07 | -0.06974 | 4.367e-05 | 3.039 | 0.002266 | -13.99 | 0.005478 | -5.489 | 1.445
[31 empty] | Angle | 50 | 100 | 5 | 10 | -1.433e-06 | -0.2846 | 4.814e-05 | 4.113 | -0.00215 | 11.35 | 0.02756 | -132.2 | 1.445
[31 empty] | Angle | 50 | 100 | 10 | 20 | -2.471e-06 | -0.06012 | 5.852e-05 | 1.869 | -0.0003479 | 3.817 | 0.009536 | -56.86 | 1.445
[31 empty] | Angle | 100 | 150 | -10 | 5 | 1.109e-06 | -0.08519 | -9.563e-05 | 3.212 | 0.001911 | -13.72 | 0.009009 | -10.44 | 1.445
[31 empty] | Angle | 100 | 150 | 5 | 10 | 6.206e-06 | -0.1108 | -0.0001211 | 3.34 | -0.0003689 | -5.13 | 0.02041 | -53.4 | 1.445
[31 empty] | Angle | 100 | 150 | 10 | 20 | 9.682e-06 | -0.2118 | -0.0001559 | 4.351 | -0.001737 | 16.92 | 0.03409 | -273.9 | 1.445
[31 empty] | Angle | 150 | 400.01 | -10 | 5 | -6.88e-06 | 0.008474 | 1.615e-05 | 2.851 | 0.001954 | -18.73 | 0.004911 | 5.113 | 1.445
[31 empty] | Angle | 150 | 400.01 | 5 | 10 | 9.08e-07 | 0.0001 | -2.279e-05 | 2.893 | 0.0003849 | -18.56 | 0.01276 | 4.264 | 1.445
[31 empty] | Angle | 150 | 400.01 | 10 | 20 | 2.403e-06 | -0.1094 | -3.774e-05 | 3.988 | -0.0003749 | -2.386 | 0.02035 | -157.5 | 1.445
[31 empty] | Globe | 50 | 100 | -10 | 5 | -6.623e-06 | -0.1071 | -2.972e-05 | 2.836 | 0.001323 | -8.358 | 0.008081 | -0.6409 | 1.445
[31 empty] | Globe | 50 | 100 | 5 | 10 | 1.186e-05 | -0.1974 | -0.0001221 | 3.287 | -0.001339 | 4.414 | 0.02139 | -64.5 | 1.445
[31 empty] | Globe | 50 | 100 | 10 | 20 | 3.085e-07 | -0.06117 | -6.626e-06 | 1.925 | -0.0003731 | 3.318 | 0.01173 | -53.54 | 1.445
[31 empty] | Globe | 100 | 150 | -10 | 5 | 1.389e-05 | -0.06255 | -5.849e-05 | 3.084 | 0.0006918 | -12.57 | 0.01054 | -10.73 | 1.445
[31 empty] | Globe | 100 | 150 | 5 | 10 | -1.028e-05 | -0.09974 | 6.238e-05 | 3.27 | 0.0001681 | -6.364 | 0.01316 | -41.76 | 1.445
[31 empty] | Globe | 100 | 150 | 10 | 20 | 2.696e-06 | -0.2057 | -6.741e-05 | 4.329 | -0.0009663 | 15.4 | 0.0245 | -259.4 | 1.445
[31 empty] | Globe | 150 | 400 | -10 | 5 | -4.261e-06 | -0.005472 | 5.032e-06 | 2.866 | 0.001301 | -14.94 | 0.008027 | -0.451 | 1.445
[31 empty] | Globe | 150 | 400 | 5 | 10 | 1.44e-06 | 0.001872 | -2.347e-05 | 2.83 | 0.0001353 | -19.95 | 0.01386 | 24.59 | 1.445
[31 empty] | Globe | 150 | 400 | 10 | 20 | -4.689e-06 | -0.07614 | 3.782e-05 | 3.61 | 0.0006764 | -6.616 | 0.008446 | -108.7 | 1.445

## ZW4000 Series
[9 empty] | Qty | Floor | Stair / Standpipe | Static Inlet (psi) | Residual Inlet (psi) | Flow (gpm) | Desired Residual Outlet Min (psi) | Desired Residual Outlet Max (psi) | Valve Setting | Actual Static Outlet | Actual Residual Outlet | Model (Part Number)
Fire Valve sizing, Factory Set Outlet Pressure
For all 2-1/2" ZW4000 series valves, hose or sprinkler
Step 1: Enter the static, residual, and flow data in the three green boxes (required) (See tabs below for other models)
Step 2: Enter desired residual outlet pressure to identify closest setting (optional)
Step 3: Outlet pressure values will appear below for each bonnet choice, then select model and closest setting
|  |  |  | Desired | [16 empty] | Angle Bodies | [8 empty] | Globe Bodies | [10 empty] | Angle Bodies |  |  |  |  | Globe Bodies |  |  |  |  | Grooved Globe Bodies | [11 empty] | Globe Bodies
| Static | Residual | Flow | Residual | [16 empty] | N | 50-300 |  | 201-300 |  | 301-400 |  | 401-500 |  | N | 50 |  | 101 |  | 201 |  | 301 |  | 401 |  | N | 50 | 201 | 301 | 401 | 50 | 101 | 201 | 301 | 401 | N | 50 |  | 101 |  | 201 |  | 301 |  | 401 |  | N | 50 | 101 | 201 | 301 | 401
| Inlet (PSI) | Inlet (PSI) | (GPM) | Outlet (PSI) | [16 empty] | 50 | 0.33 | -3.5 | 0.29 | -3.5 | 0.332 | -15.6 | 0 | 0 | 50 | 0.41 | -3.5 | 0.38 | -9 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | [9 empty] | 50 | 0.39 | -2.5 | 0.37 | -8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 50
INPUTS: | [20 empty] | 100 | 0.33 | -3.5 | 0.29 | -3.5 | 0.332 | -15.6 | 0.4 | -37 | 100 | 0.41 | -3.5 | 0.38 | -9 | 0.36 | -17 | 0.36 | -21 | 0.4 | -40 | 100 | [9 empty] | 150 | 0.39 | -2.5 | 0.39 | -11.5 | 0.31 | -10.5 | 0.26 | -6 | 0 | 0 | 150
[21 empty] | 150 | 0.32 | -2 | 0.32 | -8 | 0.318 | -13.5 | 0.35 | -29.5 | 150 | 0.37 | 2.5 | 0.38 | -9 | 0.32 | -11 | 0.3 | -12 | 0.38 | -37 | 150 | [9 empty] | 250 | 0.39 | -2.5 | 0.39 | -11.5 | 0.39 | -30.5 | 0.27 | -8.5 | 0.27 | -12.5 | 250
UL rated static | Models: ZW4000, ZW4000G, ZW4004, ZW4004G |  |  |  | Models: ZW4000IL, ZW4004IL | [15 empty] | 250 | 0.32 | -2 | 0.35 | -15.5 | 0.34 | -19 | 0.33 | -24.5 | 250 | 0.4 | -5 | 0.41 | -16.5 | 0.38 | -26 | 0.33 | -19.5 | 0.28 | -12 | 250 | [9 empty] | 350 | 0.38 | 1 | 0.32 | 13 | 0.34 | -13 | 0.28 | -12 | 0.22 | 5 | 350
inlet pressure* | Angle Body | Static | Residual | Difference | Globe Body | Static | Residual | Difference | [12 empty] | 350 | 0.44 | -44 | 0.3 | 2 | 0.3 | -5 | 0.28 | -7 | 350 | 0.38 | 2 | 0.36 | 1 | 0.42 | -40 | 0.28 | -2 | 0.36 | -40 | 350 | [9 empty] | 400 | [10 empty] | 401
for each setting: | Bonnet Type | Outlet | Outlet | to desired | Bonnet Type | Outlet | Outlet | to desired | [12 empty] | 400 | [8 empty] | 400 | [10 empty] | 401
400 PSI | N | 0 | 0 | 0 | N | 0 | 0 | 0 | [12 empty] | O | 50-300 |  | 201-300 |  | 301-400 |  | 401-500 |  | O | 50-100 |  | 101-200 |  | 201-300 |  | 301-400 |  | 401-500 |  | O | 50 | 201 | 301 | 401 | 50 | 101 | 201 | 301 | 401 | O | 50 |  | 101 |  | 201 |  | 301 |  | 401 |  | O | 50 | 101 | 201 | 301 | 401
400 PSI | O | 0 | 0 | 0 | O | 0 | 0 | 0 | [12 empty] | 50 | 0.35 | -3.5 | 0.318 | -6.9 | 0.35 | -15.5 | 0 | 0 | 50 | 0.44 | -5 | 0.375 | -6.75 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | [9 empty] | 50 | 0.43 | -4.5 | 0.38 | -9 | 0 | 0 | 0 | 0 | 0 | 0 | 50
360 PSI | P | 0 | 0 | 0 | P | 0 | 0 | 0 | [12 empty] | 100 | 0.35 | -3.5 | 0.318 | -6.9 | 0.35 | -15.5 | 0.38 | -24 | 100 | 0.44 | -5 | 0.375 | -6.75 | 0.3 | -8 | 0.38 | -20 | 0.48 | -48 | 100 | [9 empty] | 150 | 0.41 | -1.5 | 0.42 | -15 | 0.34 | -14 | 0.26 | -2 | 0 | 0 | 150
310 PSI | Q | 0 | 0 | 0 | Q | 0 | 0 | 0 | [12 empty] | 150 | 0.33 | -0.5 | 0.382 | -16.5 | 0.315 | -10.25 | 0.29 | -10.5 | 150 | 0.41 | -0.5 | 0.44 | -16.5 | 0.4 | -23 | 0.3 | -8 | 0.366 | -30.9 | 150 | [9 empty] | 250 | 0.42 | -4 | 0.43 | -17.5 | 0.43 | -36.5 | 0.3 | -12 | 0.36 | -32 | 250
290 PSI | R | 0 | 0 | 0 | R | 0 | 0 | 0 | [12 empty] | 250 | 0.39 | -15.5 | 0.36 | -11 | 0.385 | -27.75 | 0.36 | -28 | 250 | 0.46 | -13 | 0.445 | -17.75 | 0.4 | -23 | 0.33 | -15.5 | 0.334 | -22.9 | 250 | [9 empty] | 350 | 0.36 | 17 | 0.4 | -7 | 0.42 | -33 | 0.32 | -19 | 0.3 | -11 | 350
250 PSI | S | 0 | 0 | 0 | S | 0 | 0 | 0 | [12 empty] | 350 | 0.38 | -12 | 0.26 | 24 | 0.28 | 9 | 0.38 | -35 | 350 | 0.22 | 71 | 0.38 | 5 | 0.44 | -37 | 0.32 | -12 | 0.24 | 10 | 350 | [9 empty] | 400 | [10 empty] | 401
225 PSI | T | 0 | 0 | 0 | T | 0 | 0 | 0 | [12 empty] | 400 | [8 empty] | 400 | [10 empty] | 401
200 PSI | U | 0 | 0 | 0 | U | 0 | 0 | 0 | [12 empty] | P | 50-300 |  | 201-300 |  | 301-400 |  | 401-500 |  | P | 50-100 |  | 101-200 |  | 201-300 |  | 301-400 |  | 401-500 |  | P | 50 | 201 | 301 | 401 | 50 | 101 | 201 | 301 | 401 | P | 50 |  | 101 |  | 201 |  | 301 |  | 401 |  | P | 50 | 101 | 201 | 301 | 401
[21 empty] | 50 | 0.4 | -3 | 0.415 | -10.75 | 0.4 | -17 | 0 | 0 | 50 | 0.47 | -2.5 | 0.44 | -8 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | [9 empty] | 50 | 0.47 | -2.5 | 0.43 | -7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 50
| Grooved | Models: ZW4000ILG, ZW4004ILG |  |  | Floor Worksheet Instructions | [15 empty] | 100 | 0.4 | -3 | 0.415 | -10.75 | 0.4 | -17 | 0.42 | -24 | 100 | 0.47 | -2.5 | 0.44 | -8 | 0.46 | -21 | 0.44 | -23 | 0.52 | -52 | 100 | [9 empty] | 150 | 0.5 | -7 | 0.49 | -16.5 | 0.38 | -11 | 0.33 | -7.5 | 0 | 0 | 150
| Globe Body | Static | Residual | Difference | 1. Copy green input values and paste to Columns O, P, Q | [15 empty] | 150 | 0.42 | -6 | 0.405 | -9.25 | 0.41 | -18.5 | 0.36 | -15 | 150 | 0.52 | -10 | 0.51 | -18.5 | 0.4 | -12 | 0.35 | -9.5 | 0.47 | -44.5 | 150 | [9 empty] | 250 | 0.4 | 18 | 0.44545 | -5.3636 | 0.45455 | -29.6364 | 0.35455 | -13.6364 | 0.40909 | -33.2727 | 250
| Bonnet Type | Outlet | Outlet | to desired | for each floor | [15 empty] | 250 | 0.39091 | 1.2727 | 0.40909 | -10.2727 | 0.39091 | -13.7273 | 0.39091 | -22.7273 | 250 | 0.45455 | 6.3636 | 0.49091 | -13.7273 | 0.44545 | -23.3636 | 0.34545 | -8.3636 | 0.4 | -27 | 250 | [9 empty] | 360 | 0.4 | 18 | 0.44545 | -5.3636 | 0.45 | -28 | 0.35455 | -13.6364 | 0.40909 | -33.2727 | 360
400 PSI | N | 0 | 0 | 0 | 2. Copy selected Bonnet Type, Static Outlet | [15 empty] | 382 | [8 empty] | 360 | [10 empty] | 401 | [9 empty] | 400 | [10 empty] | 401
400 PSI | O | 0 | 0 | 0 | and Residual Outlet values | [15 empty] | Q | 50-300 |  | 201-300 |  | 301-400 |  | 401-500 |  | Q | 50-100 |  | 101-200 |  | 201-300 |  | 301-400 |  | 401-500 |  | Q | 50 | 201 | 301 | 401 | 50 | 101 | 201 | 301 | 401 | Q | 50 |  | 101 |  | 201 |  | 301 |  | 401 |  | Q | 50 | 101 | 201 | 301 | 401
360 PSI | P | 0 | 0 | 0 | 3. Paste values to Valve Setting, Actual Static Outlet, | [15 empty] | 50 | 0.47 | -4.5 | 0.43 | -4.5 | 0.42 | -10 | 0 | 0 | 50 | 0.56 | -4 | 0.5 | -9 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | [9 empty] | 50 | 0.565 | -5.75 | 0.49 | -8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 50
310 PSI | Q | 0 | 0 | 0 | and Actual Residual Outlet columns U, V, W | [15 empty] | 100 | 0.47 | -4.5 | 0.43 | -4.5 | 0.42 | -10 | 0.42 | -15 | 100 | 0.56 | -4 | 0.5 | -9 | 0.5 | -22 | 0.54 | -30 | 0.68 | -68 | 100 | [9 empty] | 150 | 0.51 | 2.5 | 0.54 | -16 | 0.45 | -15.5 | 0.39 | -13.5 | 0 | 0 | 150
290 PSI | R | 0 | 0 | 0 | 4. Copy and paste Part Number created from | [15 empty] | 150 | 0.45 | -1.5 | 0.44 | -6 | 0.41 | -8.5 | 0.39 | -10.5 | 150 | 0.55 | -2.5 | 0.56 | -18 | 0.465 | -16.75 | 0.37 | -4.5 | 0.5 | -41 | 150 | [9 empty] | 250 | 0.56667 | -11.6667 | 0.48333 | -1.8333 | 0.51667 | -32.1667 | 0.36667 | -7.6667 | 0.51667 | -54.1667 | 250
250 PSI | S | 0 | 0 | 0 | Part Number Assistant tab to column X | [15 empty] | 250 | 0.46667 | -5.6667 | 0.46667 | -12.6667 | 0.5 | -31 | 0.41667 | -17.1667 | 250 | 0.51667 | 5.8333 | 0.53333 | -11.3333 | 0.575 | -44.25 | 0.4 | -12 | 0.45 | -28.5 | 250 | [9 empty] | 310 | 0.56667 | -11.6667 | 0.48333 | -1.8333 | 0.46667 | -16.6667 | 0.36667 | -7.6667 | 0.51667 | -54.1667 | 310
225 PSI | T | 0 | 0 | 0 | 5. Input remaining data to columns L, M, N, R, S | [15 empty] | 340 | [8 empty] | 310 | [10 empty] | 401 | [9 empty] | 400 | [10 empty] | 401
200 PSI | U | 0 | 0 | 0 | [16 empty] | R | 50-300 |  | 201-300 |  | 301-400 |  | 401-500 |  | R | 50-100 |  | 101-200 |  | 201-300 |  | 301-400 |  | 401-500 |  | R | 50 | 201 | 301 | 401 | 50 | 101 | 201 | 301 | 401 | R | 50 |  | 101 |  | 201 |  | 301 |  | 401 |  | R | 50 | 101 | 201 | 301 | 401
NOTES: | [20 empty] | 50 | 0.53 | -4.5 | 0.52 | -8 | 0.48 | -9 | 0 | 0 | 50 | 0.62 | -5 | 0.54 | -8 | 0 | 0 | 0 | 0 | 0 | 0 | 50 | [9 empty] | 50 | 0.62 | -5 | 0.53 | -7.5 | 0 | 0 | 0 | 0 | 0 | 0 | 50
All calculated outlet pressures have a tolerance +/- 10% | [20 empty] | 100 | 0.53 | -4.5 | 0.52 | -8 | 0.48 | -9 | 0.44 | -9 | 100 | 0.62 | -5 | 0.54 | -8 | 0.6 | -29 | 0.58 | -31 | 0.9 | -90 | 100 | [9 empty] | 150 | 0.58571 | 0.14286 | 0.58571 | -15.8571 | 0.50714 | -17.0714 | 0.46429 | -18.6429 | 0.5 | -37 | 150
Static and Residual Outlet values must be below 175 PSI for UL approval (Values exceeding 175 PSI will be highlighted RED) | [20 empty] | 150 | 0.51 | -1.5 | 0.52 | -8 | 0.51 | -13.5 | 0.49 | -16.5 | 150 | 0.6 | -2 | 0.62 | -20 | 0.54 | -20 | 0.49 | -17.5 | 0.53 | -34.5 | 150 | [9 empty] | 290 | 0.58571 | 0.14286 | 0.58571 | -15.8571 | 0.5 | -15 | 0.46429 | -18.6429 | 0.5 | -37 | 290
*UL rated static inlet pressure keeps the valve outlet below 175 PSI for all flowing conditions | [20 empty] | 250 | 0.5 | 1 | 0.525 | -9.25 | 0.525 | -17.25 | 0.45 | -6.5 | 250 | 0.575 | 4.25 | 0.6 | -15 | 0.5 | -10 | 0.35 | 17.5 | 0.4 | -2 | 250 | [9 empty] | 380 | [10 empty] | 388
*When UL rated static inlet pressure is exceeded, Static Outlet values will be highlighted RED | [20 empty] | 301 | [8 empty] | 290 | [10 empty] | 388
If calculated pressure value reads zero (0), that bonnet type is not available for the inputted pressure or flow | [20 empty] | S | 50-300 |  | 201-300 |  | 301-400 |  | 401-500 |  | S | 50-100 |  | 101-200 |  | 201-300 |  | 301-400 |  | 401-500 |  | S | 50 | 201 | 301 | 401 | 50 | 101 | 201 | 301 | 401 | S | 50 |  | 101 |  | 201 |  | 301 |  | 401 |  | S | 50 | 101 | 201 | 301 | 401
Refer to Part Number Assistant tab below to get help with part numbers | [20 empty] | 50 | 0.59 | -3.5 | 0.57 | -7.5 | 0.57 | -11.5 | 0 | 0 | 50 | 0.683 | -5.45 | 0.6 | -7 | 0.45 | -9 | 0 | 0 | 0 | 0 | 50 | [9 empty] | 50 | 0.68 | -6 | 0.575 | -5.25 | 0.56 | -14 | 0 | 0 | 0 | 0 | 50
[21 empty] | 100 | 0.59 | -3.5 | 0.57 | -7.5 | 0.57 | -11.5 | 0.54 | -10 | 100 | 0.683 | -5.45 | 0.6 | -7 | 0.7 | -34 | 0.7 | -38 | 1.04 | -104 | 100 | [9 empty] | 150 | 0.62727 | 1.9091 | 0.65455 | -17.1818 | 0.54545 | -11.8182 | 0.55455 | -25.1818 | 0.50909 | -30.3636 | 150
Zurn Water, LLC ¦ Wilkins | [20 empty] | 150 | 0.58 | -2 | 0.6 | -12 | 0.52 | -4 | 0.54 | -10 | 150 | 0.72 | -11 | 0.71 | -23.5 | 0.61 | -20.5 | 0.62 | -26 | 0.64 | -44 | 150 | [9 empty] | 260 | 0.62727 | 1.9091 | 0.65455 | -17.1818 | 0.54878 | -12.6829 | 0.55455 | -25.1818 | 0.50909 | -30.3636 | 260
1747 Commerce Way, Paso Robles, CA 93446 USA | [20 empty] | 200 | 0.6 | -6 | 0.56 | -4 | 0.54 | -8 | 0.5 | -2 | 200 | 0.72 | -11 | 0.71 | -23.5 | 0.61 | -20.5 | 0.62 | -26 | 0.64 | -44 | 200 | [9 empty] | 342 | [10 empty] | 352
Ph. 855-663-9876 | [20 empty] | 270 | [8 empty] | 250 | [10 empty] | 352
ZURN.COM | [20 empty] | T | 50-200 |  | 201-300 |  | 301-400 |  | 401-500 |  | T | 50-100 |  | 101-200 |  | 201-300 |  | 301-400 |  | 401-500 |  | T | 50 | 201 | 301 | 401 | 50 | 101 | 201 | 301 | 401 | T | 50 |  | 101 |  | 201 |  | 301 |  | 401 |  | T | 50 | 101 | 201 | 301 | 401
REV 4/8/2024 | [20 empty] | 50 | 0.7 | -5 | 0.67 | -5 | 0.64 | -7 | 0 | 0 | 50 | 0.76 | -6 | 0.64 | -3 | 0.64 | -11 | 0.66 | -23 | 0 | 0 | 50 | [9 empty] | 50 | 0.76 | -6 | 0.69 | -5.5 | 0.7 | -14 | 0.66 | -23 | 0 | 0 | 50
[21 empty] | 100 | 0.72 | -7 | 0.68 | -6 | 0.72 | -15 | 0.74 | -21 | 100 | 0.76 | -6 | 0.74 | -13 | 0.76 | -23 | 0.66 | -23 | 0.62 | -32 | 100 | [9 empty] | 150 | 0.69333 | 4 | 0.69333 | -6 | 0.62667 | -3 | 0.72 | -32 | 0.66667 | -39 | 150
[21 empty] | 150 | 0.6 | 11 | 0.66 | -3 | 0.66 | -6 | 0.64 | -6 | 150 | 0.68 | 6 | 0.68 | -4 | 0.66 | -8 | 0.74 | -35 | 0.64 | -35 | 150 | [9 empty] | 225 | 0.69333 | 4 | 0.69333 | -6 | 0.61667 | -0.75 | 0.72 | -32 | 0.66667 | -39 | 225
[21 empty] | 200 | 0.7 | -9 | 0.7 | -11 | 0.64 | -2 | 0.64 | -6 | 200 | 0.72 | -2 | 0.72 | -12 | 0.56 | 12 | 0.68 | -23 | 0.72 | -51 | 200 | [9 empty] | 285 | [10 empty] | 307
[21 empty] | 237 | [8 empty] | 225 | [10 empty] | 307
[21 empty] | U | 50-200 |  | 201-300 |  | 301-400 |  | 401-500 |  | U | 50-100 |  | 101-200 |  | 201-300 |  | 301-400 |  | 401-500 |  | U | 50 | 201 | 301 | 401 | 50 | 101 | 201 | 301 | 401 | U | 50 |  | 101 |  | 201 |  | 301 |  | 401 |  | U | 50 | 101 | 201 | 301 | 401
[21 empty] | 50 | 0.76 | -2 | 0.84 | -12 | 0.78 | -11 | 0 | 0 | 50 | 0.82 | -5 | 0.8 | -7 | 0.816 | -16.6 | 0.72 | -18 | 0 | 0 | 50 | [9 empty] | 50 | 0.82 | -5 | 0.77 | -5.5 | 0.788 | -15.2 | 0.76 | -20 | 0.78 | -39 | 50
[21 empty] | 100 | 0.74 | 0 | 0.72 | 0 | 0.78 | -11 | 0.78 | -16 | 100 | 0.82 | -5 | 0.74 | -1 | 0.76 | -11 | 0.8 | -26 | 0.76 | -36 | 100 | [9 empty] | 150 | 0.8 | -2 | 0.78 | -7 | 0.82 | -20 | 0.72 | -14 | 0.74 | -33 | 150
[21 empty] | 150 | 0.78 | -6 | 0.8 | -12 | 0.8 | -14 | 0.8 | -19 | 150 | 0.8 | -2 | 0.78 | -7 | 0.82 | -20 | 0.72 | -14 | 0.74 | -33 | 150 | [9 empty] | 200 | 0.8 | -2 | 0.78 | -7 | 0.7561 | -7.2195 | 0.72 | -14 | 0.74 | -33 | 200
[21 empty] | 222 | [8 empty] | 200 | [10 empty] | 287 | [9 empty] | 241 | [10 empty] | 287
static
[21 empty] | n | 2.8433 | -12.4791
[21 empty] | o | 2.5753 | -9.5859
[21 empty] | p | 2.1739 | 2.1739
[21 empty] | q | 2 | -9.3334
[21 empty] | r | 1.7292 | -0.8646
[21 empty] | s | 1.6305 | -14.8557
[21 empty] | t | 1.398 | -7.2
[21 empty] | u | 1.2995 | -5.05

## ZW4100 Series
[6 empty] | Qty | Floor | Stair / Standpipe | Static Inlet (psi) | Residual Inlet (psi) | Flow (gpm) | Desired Residual Outlet Min (psi) | Desired Residual Outlet Max (psi) | Valve Setting | Actual Static Outlet | Actual Residual Outlet | Model (Part Number)
Fire Valve sizing, Factory Set
For all 1-1/2" ZW4100 series valves, hose or sprinkler
Step 1: Enter the static, residual, and flow data in the three green boxes (required) (See tabs below for other models)
Step 2: Enter desired residual outlet pressure to identify closest setting (optional)
Step 3: Outlet pressure values will appear below for each bonnet choice, then select model and closest setting
|  |  |  | Desired | [13 empty] | Angle Bodies | [10 empty] | Angle Bodies
| Static | Residual | Flow | Residual | [13 empty] | J | 25-75 |  | 76-125 |  | 126-150 |  | 151-175 |  | 176-200 |  | J | 25 | 76 | 126 | 151 | 176
| Inlet (psi) | Inlet (psi) | (gpm) | Outlet | [13 empty] | 50 | 0.22 | 0 | [8 empty] | 50
[18 empty] | 100 | 0.22 | 0 | 0.17 | 0 | 0.165 | 0 |  |  |  |  | 100
[18 empty] | 200 | 0.28 | -12 | 0.28 | -22 | 0.19 | -5 | 0.18667 | 0 | 0.18 | 0 | 200
UL rated static | Models: ZW4100, ZW4100G, ZW4104, ZW4104G | [16 empty] | 300 | 0.33 | -27 | 0.31 | -31 | 0.26 | -26 | 0.16 | 8 | 0.22 | -12 | 300
inlet pressure* | Angle Body | Static | Residual | Difference | Floor Worksheet Instructions | [12 empty] | 401 | [10 empty] | 401
for each setting: | Bonnet Type | Outlet | Outlet | to desired | 1. Copy green input values and paste to Columns J, K, L
400 PSI | J | 0 | 0 | 0 | for each floor | [12 empty] | K | 25-75 |  | 76-125 |  | 126-150 |  | 151-175 |  | 176-200 |  | K | 25 | 76 | 126 | 151 | 176
400 PSI | K | 0 | 0 | 0 | 2. Copy selected Bonnet Type, Static Outlet | [12 empty] | 50 | 0.26 | -3 | 0.17 | 0 | [6 empty] | 50
400 PSI | L | 0 | 0 | 0 | and Residual Outlet values | [12 empty] | 100 | 0.34 | -11 | 0.23 | -6 | 0.185 | 0 |  |  |  |  | 100
360 PSI | M | 0 | 0 | 0 | 3. Paste values to Valve Setting, Actual Static Outlet, | [12 empty] | 200 | 0.33 | -9 | 0.34 | -28 | 0.25 | -13 | 0.23 | 0 | 0.20333 | 0 | 200
325 PSI | N | 0 | 0 | 0 | and Actual Residual Outlet columns P, Q, R | [12 empty] | 300 | 0.37 | -21 | 0.35 | -31 | 0.3 | -28 | 0.21 | 6 | 0.29 | -26 | 300
290 PSI | O | 0 | 0 | 0 | 4. Copy and paste Part Number created from | [12 empty] | 401 | [10 empty] | 401
240 PSI | P | 0 | 0 | 0 | Part Number Assistant tab to column S
200 PSI | Q | 0 | 0 | 0 | 5. Input remaining data to columns G, H, I, M, N | [12 empty] | L | 25-75 |  | 76-125 |  | 126-150 |  | 151-175 |  | 176-200 |  | L | 25 | 76 | 126 | 151 | 176
[18 empty] | 50 | 0.36 | -8 | 0.18 | 0 | [6 empty] | 50
NOTES: | [17 empty] | 100 | 0.35 | -7 | 0.3 | -12 | 0.235 | -3 |  |  |  |  | 100
All calculated outlet pressures have a tolerance +/- 10% | [17 empty] | 200 | 0.4 | -17 | 0.41 | -34 | 0.34 | -24 | 0.27 | -6 | 0.26333 | -6 | 200
Static and Residual Outlet values must be below 175 PSI for UL approval (Values exceeding 175 PSI will be highlighted RED) | [17 empty] | 300 | 0.43 | -26 | 0.41 | -34 | 0.32 | -18 | 0.3 | -15 | 0.29 | -14 | 300
*UL rated static inlet pressure keeps the valve outlet below 175 PSI for all flowing conditions | [17 empty] | 401 | [10 empty] | 401
*When UL rated static inlet pressure is exceeded, Static Outlet values will be highlighted RED | [17 empty] | M | 25-75 |  | 76-125 |  | 126-150 |  | 151-175 |  | 176-200 |  | M | 25 | 76 | 126 | 151 | 176
If calculated pressure value reads zero (0), that bonnet type is not available for the inputted pressure or flow | [17 empty] | 50 | 0.34 | -5 | 0.36 | -9 | [6 empty] | 50
Refer to Part Number Assistant tab below to get help with part numbers | [17 empty] | 100 | 0.44 | -15 | 0.31 | -4 | 0.26 | 0 | 0.27 | -3 |  |  | 100
[18 empty] | 200 | 0.46 | -19 | 0.42 | -26 | 0.35 | -18 | 0.4 | -29 | 0.32 | -6 | 200
Zurn Water, LLC ¦ Wilkins | [17 empty] | 300 | 0.5 | -31 | 0.46667 | -40 | 0.35 | -18 | 0.4 | -29 | 0.41667 | -35 | 300
1747 Commerce Way, Paso Robles, CA 93446 USA | [17 empty] | 361 | [10 empty] | 361
Ph. 855-663-9876 | [17 empty] | N | 25-75 |  | 76-125 |  | 126-150 |  | 151-175 |  | 176-200 |  | N | 25 | 76 | 126 | 151 | 176
ZURN.COM | [17 empty] | 50 | 0.48 | -10 | 0.3 | 0 | [6 empty] | 50
REV 4/8/2024 | [17 empty] | 100 | 0.45333 | -7.3333 | 0.38667 | -8.6667 | 0.29714 | 0 | 0.27429 | 0 |  |  | 100
[18 empty] | 175 | 0.50667 | -16.6667 | 0.41333 | -13.3333 | 0.38667 | -15.6667 | 0.44 | -29 | 0.36 | -10 | 175
[18 empty] | 250 | 0.54667 | -26.6667 | 0.50667 | -36.6667 | 0.44 | -29 | 0.49333 | -42.3333 | 0.50667 | -46.6667 | 250
[18 empty] | 326 | [10 empty] | 326
[18 empty] | O | 25-75 |  | 76-125 |  | 126-150 |  | 151-175 |  | 176-200 |  | O | 25 | 76 | 126 | 151 | 176
[18 empty] | 50 | 0.44 | -4 | 0.37 | -2 | [6 empty] | 50
[18 empty] | 100 | 0.55 | -15 | 0.46667 | -11.6667 | 0.34375 | 0 | 0.30625 | 0 |  |  | 100
[18 empty] | 160 | 0.55714 | -16.1429 | 0.45714 | -10.1429 | 0.47143 | -20.4286 | 0.48571 | -28.7143 | 0.4087 | -16 | 160
[18 empty] | 230 | 0.58333 | -22.1667 | 0.55 | -31.5 | 0.45 | -15.5 | 0.68333 | -74.1667 | 0.66667 | -75.3333 | 230
[18 empty] | 291 | [10 empty] | 291
[18 empty] | P | 25-75 |  | 76-125 |  | 126-150 |  | 151-175 |  | 176-200 |  | P | 25 | 76 | 126 | 151 | 176
[18 empty] | 50 | 0.6 | -9 | 0.64 | -15 | 0.4 | -1 |  |  |  |  | 50
[18 empty] | 100 | 0.56 | -5 | 0.56 | -7 | 0.56 | -17 | 0.39333 | 0 | 0.34 | 0 | 100
[18 empty] | 150 | 0.66 | -20 | 0.6 | -13 | 0.58 | -20 | 0.72 | -49 | 0.66 | -48 | 150
[18 empty] | 200 | 0.675 | -23 | 0.775 | -48 | 0.625 | -29 | 0.625 | -30 | 0.675 | -51 | 200
[18 empty] | 241 | [10 empty] | 241
[18 empty] | Q | 25-75 |  | 76-125 |  | 126-150 |  | 151-175 |  | 176-200 |  | Q | 25 | 76 | 126 | 151 | 176
[18 empty] | 50 | 0.96667 | -19.3333 | 1 | -31 | 0.49167 | -3.3333 |  |  |  |  | 50
[18 empty] | 80 | 0.65 | 6 | 0.725 | -9 | 0.825 | -30 | 0.5 | 0 | 0.43333 | 0 | 80
[18 empty] | 120 | 0.75 | -6 | 0.8 | -18 | 0.8 | -27 | 0.8 | -36 | 0.75 | -38 | 120
[18 empty] | 160 | 0.85 | -22 | 0.85 | -26 | 0.775 | -23 | 0.775 | -32 | 0.725 | -34 | 160
[18 empty] | 201 | [10 empty] | 201
[18 empty] | J | 3.34 | -7.098
[18 empty] | K | 2.8686 | -12.031
[18 empty] | L | 2.5119 | -11.386
[18 empty] | M | 2.1465 | -7.565
[18 empty] | N | 1.9351 | -14
[18 empty] | O | 1.6996 | -7.808
[18 empty] | P | 1.4239 | -9
[18 empty] | Q | 1.1799 | -7

## Z3000 Series
[9 empty] | Qty | Floor | Stair / Standpipe | Static Inlet (psi) | Residual Inlet (psi) | Flow (gpm) | Desired Residual Outlet Min (psi) | Desired Residual Outlet Max (psi) | Valve Setting | Actual Static Outlet | Actual Residual Outlet | Model (Part Number)
|  | Fire Valve sizing, Adjustable Outlet Pressure | [19 empty] | 191 | 400 | 0 | A | 3/8 | 3.483 | -35.417 |  | 0 | 0
For all Z3000 series valves, hose or sprinkler | [21 empty] | 135 | 400 | 0 | B | 1/2 | 3.442 | -88.701 |  | 0 | 0
Step 1: Enter the static, residual, and flow data in the three green boxes (required) (See tabs below for other models) | [21 empty] | 100 | 400 | 0 | C | 5/8 | 3.409 | -135.227 |  | 0 | 0
Step 2: Enter desired residual outlet pressure to identify closest setting (optional) | [21 empty] | 100 | 400 | 0 | D | 11/16 | 3.371 | -149.438 |  | 0 | 0
Step 3: Outlet pressure values will appear below for each setting choice, then select model and closest setting | [21 empty] | 100 | 400 | 0 | E | 3/4 | 3.571 | -196.429 |  | 0 | 0
|  |  |  | Desired | [17 empty] | 100 | 400 | 0 | F | 13/16 | 3.614 | -228.916 |  | 0 | 0
| Static | Residual | Flow | Residual | [16 empty] | 400 | 100 | 365 | 0 | G | 7/8 | 3.533 | -253.333 |  | 0 | 0
| Inlet (psi) | Inlet (psi) | (gpm) | Outlet | [17 empty] | 100 | 150 | 0 | H | 15/16 | 2.5 | -150 |  | 0 | 0
[21 empty] | 400 | 150 | 340 | 0 | H | 15/16 | 3.436 | -262.363 |  | 0 | 0
[22 empty] | 100 | 119 | 0 | I | 1 | 1.9 | -90 |  | 0 | 0
| Models: Z3000, Z3004, Z3005 |  |  |  | Models: Z3000IL, Z3005IL, Z3004IL | [16 empty] | 119 | 143 | 0 | I | 1 | 2.4 | -145 |  | 0 | 0
| Angle |  |  |  | Globe | [15 empty] | 400 | 143 | 330 | 0 | I | 1 | 3.4 | -265 |  | 0 | 0
| Bodies | Static | Residual | Difference | Bodies | Static | Residual | Difference | [13 empty] | 100 | 130 | 0 | J | 1-1/16 | 1 | 0 |  | 0 | 0
| Setting | Outlet | Outlet | to desired | Setting | Outlet | Outlet | to desired | [13 empty] | 130 | 145 | 0 | J | 1-1/16 | 2.143 | -148.571 |  | 0 | 0
| A | 0 | 0 | 0 | A | 0 | 0 | 0 | [13 empty] | 145 | 176 | 0 | J | 1-1/16 | 3.875 | -385.875 |  | 0 | 0
| B | 0 | 0 | 0 | B | 0 | 0 | 0 | [12 empty] | 400 | 176 | 300 | 0 | J | 1-1/16 | 4.133 | -423.333 |  | 0 | 0
| C | 0 | 0 | 0 | C | 0 | 0 | 0 | [13 empty] | 100 | 140 | 0 | K | 1-1/8 | 1 | 0 |  | 0 | 0
| D | 0 | 0 | 0 | D | 0 | 0 | 0 | [12 empty] | 349 | 140 | 262 | 0 | K | 1-1/8 | 3.486 | -348 |  | 0 | 0
| E | 0 | 0 | 0 | E | 0 | 0 | 0 | [13 empty] | 100 | 148 | 0 | L | 1-3/16 | 1 | 0 |  | 0 | 0
| F | 0 | 0 | 0 | F | 0 | 0 | 0 | [12 empty] | 252 | 148 | 200 | 0 | L | 1-3/16 | 2.08 | -164 |  | 0 | 0
| G | 0 | 0 | 0 | G | 0 | 0 | 0 | [13 empty] | 50 | 205 | 50 | A | 3/8 | 3.69 | -34.881 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 101 | 50 | A | 2.6 | 4.8 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 102 | 50 | A | 2.65 | -17.25 | 0 | 0 | 0 | 0 | 0 | 0
| H | 0 | 0 | 0 | H | 0 | 0 | 0 | [13 empty] | 205 | 260 | 50 | A | 3/8 | 3.666 | -33.333 | 0 | 0 | 0 | 0 | 0 | 0 |  | 101 | 201 | 50 | A | 3.8462 | -41.3077 | 0 | 0 | 0 | 0 | 0 | 0 |  | 102 | 199 | 50 | A | 3.3448 | -48.5172 | 0 | 0 | 0 | 0 | 0 | 0
| I | 0 | 0 | 0 | I | 0 | 0 | 0 | [13 empty] | 260 | 300 | 50 | A | 3/8 | 4 | -60 | 0 | 0 | 0 | 0 | 0 | 0 |  | 201 | 304 | 50 | A | 4.9048 | -108 | 0 | 0 | 0 | 0 | 0 | 0 |  | 199 | 300 | 50 | A | 3.6071 | -67.9286 | 0 | 0 | 0 | 0 | 0 | 0
| J | 0 | 0 | 0 | J | 0 | 0 | 0 | [13 empty] | 300 | 400 | 50 | A | 3/8 | 4.545 | -109.09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 304 | 400 | 50 | A | 4.7619 | -96 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 50 | A | 5.2632 | -236.8421 | 0 | 0 | 0 | 0 | 0 | 0
| K | 0 | 0 | 0 | K | 0 | 0 | 0 | [13 empty] | 50 | 233 | 100 | A | 3/8 | 3.66 | -4.9 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 100 | A | 2.6316 | 10.5263 | 0 | 0 | 0 | 0 | 0 | 0 |  | 50 | 98 | 100 | A | 2.7222 | 0 | 0 | 0 | 0 | 0 | 0 | 0
| L | 0 | 0 | 0 | L | 0 | 0 | 0 | [13 empty] | 233 | 325 | 100 | A | 3/8 | 3.833 | -16.166 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 202 | 100 | A | 3.9231 | -33.3846 | 0 | 0 | 0 | 0 | 0 | 0 |  | 98 | 198 | 100 | A | 3.125 | -14.5 | 0 | 0 | 0 | 0 | 0 | 0
| Models: Z3000ILG, Z3004ILG | [20 empty] | 325 | 400 | 100 | A | 3/8 | 3.9474 | -26.316 | 0 | 0 | 0 | 0 | 0 | 0 |  | 202 | 303 | 100 | A | 5.05 | -101 | 0 | 0 | 0 | 0 | 0 | 0 |  | 198 | 302 | 100 | A | 3.25 | -23 | 0 | 0 | 0 | 0 | 0 | 0
| Globe Grooved | [20 empty] | 50 | 240 | 150 | A | 3/8 | 3.393 | 19.464 | 0 | 0 | 0 | 0 | 0 | 0 |  | 303 | 400 | 100 | A | 4.8095 | -81.7619 | 0 | 0 | 0 | 0 | 0 | 0 |  | 302 | 400 | 100 | A | 3.3103 | -29.0345 | 0 | 0 | 0 | 0 | 0 | 0
| Bodies | Static | Residual | Difference | Floor Worksheet Instructions | [16 empty] | 240 | 290 | 150 | A | 3/8 | 3.333 | 23.333 | 0 | 0 | 0 | 0 | 0 | 0 |  | 68 | 99 | 150 | A | 3.4138 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 70 | 99 | 150 | A | 2.8235 | 17.1176 | 0 | 0 | 0 | 0 | 0 | 0
| Setting | Outlet | Outlet | to desired | 1. Copy green input values and paste to Columns O, P, Q | [16 empty] | 290 | 400 | 150 | A | 3/8 | 4.074 | -35.926 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99 | 200 | 150 | A | 3.7407 | -9.4815 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99 | 197 | 150 | A | 3.2667 | 4.2667 | 0 | 0 | 0 | 0 | 0 | 0
| A | 0 | 0 | 0 | for each floor | [16 empty] | 248 | 264 | 200 | A | 3/8 | 3.2 | 40 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 304 | 150 | A | 5.2 | -91.2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 197 | 299 | 150 | A | 3.1875 | 8.9375 | 0 | 0 | 0 | 0 | 0 | 0
| B | 0 | 0 | 0 | 2. Copy selected Setting, Static Outlet | [16 empty] | 264 | 300 | 200 | A | 3/8 | 3.6 | 12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 304 | 400 | 150 | A | 4.3333 | -25.3333 | 0 | 0 | 0 | 0 | 0 | 0 |  | 299 | 400 | 150 | A | 3.2 | 7.8 | 0 | 0 | 0 | 0 | 0 | 0
| C | 0 | 0 | 0 | and Residual Outlet values | [16 empty] | 300 | 340 | 200 | A | 3/8 | 3.636 | 9.09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 85 | 97 | 200 | A | 4.4091 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99 | 198 | 200 | A | 3.2333 | 29.8667 | 0 | 0 | 0 | 0 | 0 | 0
| D | 0 | 0 | 0 | 3. Paste values to Valve Setting, Actual Static Outlet, | [16 empty] | 340 | 400 | 200 | A | 3/8 | 4.286 | -50 | 0 | 0 | 0 | 0 | 0 | 0 |  | 97 | 198 | 200 | A | 3.4828 | 20.3793 | 0 | 0 | 0 | 0 | 0 | 0 |  | 198 | 299 | 200 | A | 3.3667 | 22.9333 | 0 | 0 | 0 | 0 | 0 | 0
| E | 0 | 0 | 0 | and Actual Residual Outlet columns U, V, W | [16 empty] | 258 | 300 | 250 | A | 3/8 | 3.818 | 9.818 | 0 | 0 | 0 | 0 | 0 | 0 |  | 198 | 301 | 200 | A | 4.9048 | -52.1429 | 0 | 0 | 0 | 0 | 0 | 0 |  | 299 | 400 | 200 | A | 3.3667 | 22.9333 | 0 | 0 | 0 | 0 | 0 | 0
| F | 0 | 0 | 0 | 4. Copy and paste Part Number created from | [16 empty] | 300 | 358 | 250 | A | 3/8 | 3.866 | 6.133 | 0 | 0 | 0 | 0 | 0 | 0 |  | 301 | 400 | 200 | A | 4.45 | -19.4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 110 | 200 | 250 | A | 3.3448 | 46.1379 | 0 | 0 | 0 | 0 | 0 | 0
| G | 0 | 0 | 0 | Part Number Assistant tab to column S | [16 empty] | 358 | 400 | 250 | A | 3/8 | 6 | -188 | 0 | 0 | 0 | 0 | 0 | 0 |  | 110 | 101 | 250 | A | 5.9412 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 250 | A | 3.4483 | 41.3793 | 0 | 0 | 0 | 0 | 0 | 0
| H | 0 | 0 | 0 | 5. Input remaining data to columns L, M, N, R, S | [16 empty] | 292 | 318 | 300 | A | 3/8 | 4.333 | 10.333 | 0 | 0 | 0 | 0 | 0 | 0 |  | 101 | 200 | 250 | A | 3.1935 | 46.7097 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 250 | A | 3.3333 | 50 | 0 | 0 | 0 | 0 | 0 | 0
| I | 0 | 0 | 0 | [17 empty] | 318 | 334 | 300 | A | 3/8 | 4 | 34 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 298 | 250 | A | 5.4444 | -61.3333 | 0 | 0 | 0 | 0 | 0 | 0 |  | 125 | 202 | 300 | A | 4.04 | 44.44 | 0 | 0 | 0 | 0 | 0 | 0
| J | 0 | 0 | 0 | [17 empty] | 334 | 400 | 300 | A | 3/8 | 5.5 | -78.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 298 | 400 | 250 | A | 4.5152 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 202 | 302 | 300 | A | 4 | 46 | 0 | 0 | 0 | 0 | 0 | 0
| K | 0 | 0 | 0 | [17 empty] | 335 | 400 | 350 | A | 3/8 | 6.5 | -87.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 196 | 300 | 300 | A | 4 | 40 | 0 | 0 | 0 | 0 | 0 | 0 |  | 302 | 400 | 300 | A | 4.0833 | 40.6667 | 0 | 0 | 0 | 0 | 0 | 0
| L | 0 | 0 | 0 | [17 empty] | 370 | 400 | 400 | A | 3/8 | 7.5 | -117.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 300 | A | 4.6154 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 199 | 303 | 350 | A | 3.9615 | 81.1538 | 0 | 0 | 0 | 0 | 0 | 0
NOTES: | [21 empty] | 50 | 170 | 50 | B | 1/2 | 3.158 | -35.263 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 304 | 350 | A | 4 | 68 | 0 | 0 | 0 | 0 | 0 | 0 |  | 303 | 400 | 350 | A | 4.4091 | 56.0909 | 0 | 0 | 0 | 0 | 0 | 0
All calculated outlet pressures have a tolerance +/- 10% | [21 empty] | 170 | 258 | 50 | B | 1/2 | 3.385 | -50 | 0 | 0 | 0 | 0 | 0 | 0 |  | 304 | 400 | 350 | A | 5.1525 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 199 | 297 | 400 | A | 5.1579 | 64.8947 | 0 | 0 | 0 | 0 | 0 | 0
Static and Residual Outlet values must be below 175 PSI for UL approval (Values exceeding 175 PSI will be highlighted RED) | [21 empty] | 258 | 400 | 50 | B | 1/2 | 4.581 | -158.839 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 298 | 400 | A | 3.88 | 111.76 | 0 | 0 | 0 | 0 | 0 | 0 |  | 297 | 400 | 400 | A | 4.4783 | 95.4783 | 0 | 0 | 0 | 0 | 0 | 0
Refer to Part Number Assistant tab below to get help with part numbers | [21 empty] | 50 | 194 | 100 | B | 1/2 | 3.2 | -14 | 0 | 0 | 0 | 0 | 0 | 0 |  | 298 | 400 | 400 | A | 6.2083 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 199 | 287 | 450 | A | 3.9091 | 126.7273 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 194 | 248 | 100 | B | 1/2 | 3.6 | -40 | 0 | 0 | 0 | 0 | 0 | 0 |  | 288 | 400 | 450 | A | 7.3846 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 287 | 400 | 450 | A | 4.7083 | 93.9583 | 0 | 0 | 0 | 0 | 0 | 0
Zurn Water, LLC ¦ Wilkins | [21 empty] | 248 | 400 | 100 | B | 1/2 | 4.108 | -80.648 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 98 | 50 | B | 2.0417 | -8.1667 | 0 | 0 | 0 | 0 | 0 | 0 |  | 234 | 249 | 500 | A | 3 | 177 | 0 | 0 | 0 | 0 | 0 | 0
1747 Commerce Way, Paso Robles, CA 93446 USA | [21 empty] | 50 | 216 | 150 | B | 1/2 | 3.388 | -4.204 | 0 | 0 | 0 | 0 | 0 | 0 |  | 98 | 203 | 50 | B | 3.3871 | -78.129 | 0 | 0 | 0 | 0 | 0 | 0 |  | 249 | 400 | 500 | A | 3.9737 | 153.6316 | 0 | 0 | 0 | 0 | 0 | 0
Ph. 855-663-9876 | [21 empty] | 216 | 266 | 150 | B | 1/2 | 3.333 | -0.666 | 0 | 0 | 0 | 0 | 0 | 0 |  | 203 | 299 | 50 | B | 3.6923 | -103.4615 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 50 | B | 2.5641 | -39.7436 | 0 | 0 | 0 | 0 | 0 | 0
ZURN.COM | [21 empty] | 266 | 345 | 150 | B | 1/2 | 3.95 | -50 | 0 | 0 | 0 | 0 | 0 | 0 |  | 299 | 400 | 50 | B | 4.2083 | -159.7083 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 50 | B | 3.3333 | -81.6667 | 0 | 0 | 0 | 0 | 0 | 0
REV 4/8/2024 | [21 empty] | 345 | 400 | 150 | B | 1/2 | 4.583 | -113.333 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 101 | 100 | B | 2.125 | -3.125 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 50 | B | 3.4483 | -91.3793 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 230 | 280 | 200 | B | 1/2 | 3.333 | 13.333 | 0 | 0 | 0 | 0 | 0 | 0 |  | 101 | 202 | 100 | B | 3.3667 | -63.9667 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 50 | B | 5.0378 | -271.7884 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 280 | 356 | 200 | B | 1/2 | 3.8 | -24 | 0 | 0 | 0 | 0 | 0 | 0 |  | 202 | 298 | 100 | B | 3.6923 | -89.6923 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 100 | B | 2.5641 | -15.3846 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 356 | 400 | 200 | B | 1/2 | 4.4 | -84 | 0 | 0 | 0 | 0 | 0 | 0 |  | 298 | 400 | 100 | B | 4.08 | -130.4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 100 | B | 2.9197 | -31.3869 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 245 | 260 | 250 | B | 1/2 | 3 | 50 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 101 | 150 | B | 2.3333 | -1.6667 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 100 | B | 3.1008 | -45.7364 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 260 | 300 | 250 | B | 1/2 | 4 | -20 | 0 | 0 | 0 | 0 | 0 | 0 |  | 101 | 201 | 150 | B | 3.4483 | -50.7241 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 100 | B | 3.4904 | -89.1798 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 300 | 400 | 250 | B | 1/2 | 4.166 | -33.333 | 0 | 0 | 0 | 0 | 0 | 0 |  | 201 | 299 | 150 | B | 3.6296 | -63.963 | 0 | 0 | 0 | 0 | 0 | 0 |  | 55 | 100 | 150 | B | 2.5 | 8.75 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 275 | 320 | 300 | B | 1/2 | 4.5 | -17.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 299 | 400 | 150 | B | 4.04 | -105 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 150 | B | 3.0303 | -10.6061 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 320 | 400 | 300 | B | 1/2 | 5.333 | -80 | 0 | 0 | 0 | 0 | 0 | 0 |  | 60 | 98 | 200 | B | 2.2857 | 15.7143 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 150 | B | 2.963 | -5.9259 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 314 | 400 | 350 | B | 1/2 | 5.375 | -35.375 | 0 | 0 | 0 | 0 | 0 | 0 |  | 98 | 199 | 200 | B | 3.2581 | -19.2903 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 150 | B | 3.2 | -30.4 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 320 | 400 | 400 | B | 1/2 | 6.154 | -80 | 0 | 0 | 0 | 0 | 0 | 0 |  | 199 | 303 | 200 | B | 3.7143 | -49.8571 | 0 | 0 | 0 | 0 | 0 | 0 |  | 80 | 100 | 200 | B | 2.0833 | 38.5417 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 138 | 50 | C | 5/8 | 2.933 | -52.667 | 0 | 0 | 0 | 0 | 0 | 0 |  | 303 | 400 | 200 | B | 3.7308 | -51.4231 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 200 | B | 3.1008 | 8.5271 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 138 | 194 | 50 | C | 5/8 | 3.294 | -76.118 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 250 | B | 3.125 | 6.25 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 200 | B | 3.2258 | 0.80645 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 194 | 260 | 50 | C | 5/8 | 3.882 | -124.353 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 301 | 250 | B | 3.8846 | -40.8462 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 200 | B | 3.2 | 3.2 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 260 | 300 | 50 | C | 5/8 | 4 | -136 | 0 | 0 | 0 | 0 | 0 | 0 |  | 301 | 400 | 250 | B | 3.8077 | -34.0769 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99 | 200 | 250 | B | 3.3898 | 16.9492 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 300 | 400 | 50 | C | 5/8 | 4.348 | -173.913 | 0 | 0 | 0 | 0 | 0 | 0 |  | 95 | 198 | 300 | B | 3.0606 | 35.7879 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 250 | B | 3.252 | 24.3902 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 160 | 100 | C | 5/8 | 2.821 | -23.333 | 0 | 0 | 0 | 0 | 0 | 0 |  | 198 | 304 | 300 | B | 3.4194 | 16.7742 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 250 | B | 3.2362 | 25.7282 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 160 | 200 | 100 | C | 5/8 | 3.333 | -56.666 | 0 | 0 | 0 | 0 | 0 | 0 |  | 304 | 400 | 300 | B | 3.619 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 98 | 200 | 300 | B | 3.8835 | 21.3592 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 200 | 260 | 100 | C | 5/8 | 3.75 | -88.75 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 301 | 350 | B | 3.2258 | 59.0645 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 300 | B | 3.6364 | 32.7273 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 260 | 331 | 100 | C | 5/8 | 4.177 | -128.412 | 0 | 0 | 0 | 0 | 0 | 0 |  | 301 | 400 | 350 | B | 4.0133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 300 | B | 3.9216 | 11.7647 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 331 | 400 | 100 | C | 5/8 | 4.929 | -211.143 | 0 | 0 | 0 | 0 | 0 | 0 |  | 198 | 304 | 400 | B | 3.3125 | 85.375 | 0 | 0 | 0 | 0 | 0 | 0 |  | 199 | 300 | 350 | B | 3.8462 | 47.1154 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 195 | 150 | C | 5/8 | 3.295 | -19.205 | 0 | 0 | 0 | 0 | 0 | 0 |  | 304 | 400 | 400 | B | 4.6061 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 350 | B | 4.2105 | 23.1579 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 195 | 250 | 150 | C | 5/8 | 3.666 | -43.333 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 288 | 450 | B | 3.2593 | 115.2593 | 0 | 0 | 0 | 0 | 0 | 0 |  | 199 | 300 | 400 | B | 4.5455 | 43.1818 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 250 | 330 | 150 | C | 5/8 | 4 | -70 | 0 | 0 | 0 | 0 | 0 | 0 |  | 288 | 400 | 450 | B | 5.434 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 400 | B | 4.1667 | 64.5833 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 330 | 400 | 150 | C | 5/8 | 4.375 | -107.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 50 | C | 1.9615 | -29.4615 | 0 | 0 | 0 | 0 | 0 | 0 |  | 199 | 300 | 450 | B | 4.1237 | 84.5361 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 213 | 263 | 200 | C | 5/8 | 3.333 | -3.6667 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 50 | C | 3.4483 | -127.5862 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 450 | B | 4.4248 | 68.8053 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 263 | 338 | 200 | C | 5/8 | 3.75 | -37 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 50 | C | 4.3478 | -213.0435 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 500 | B | 3.5714 | 132.1429 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 338 | 400 | 200 | C | 5/8 | 4.429 | -104.857 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 50 | C | 3.7037 | -137.037 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 500 | B | 3.8685 | 118.1818 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 230 | 320 | 250 | C | 5/8 | 3.6 | -4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 100 | C | 2.3636 | -37.0909 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 50 | C | 2.6316 | -68.4211 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 320 | 400 | 250 | C | 5/8 | 4.444 | -80 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 100 | C | 3.2258 | -87.0968 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 50 | C | 3.2258 | -106.4516 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 260 | 330 | 300 | C | 5/8 | 4.666 | -43.333 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 100 | C | 4 | -156 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 50 | C | 3.3333 | -116.6667 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 330 | 400 | 300 | C | 5/8 | 5 | -70 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 100 | C | 3.8462 | -138.4615 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 50 | C | 4.8309 | -303.8647 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 296 | 320 | 350 | C | 5/8 | 4.8 | -16 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 150 | C | 2.5 | -32.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 100 | C | 2.381 | -28.5714 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 320 | 400 | 350 | C | 5/8 | 5.714 | -80 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 150 | C | 3.125 | -65.625 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 100 | C | 2.7397 | -47.9452 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 287 | 333 | 400 | C | 5/8 | 4.6 | -12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 150 | C | 4 | -140 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 100 | C | 3.0769 | -78.4615 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 333 | 400 | 400 | C | 5/8 | 5.583 | -85.75 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 150 | C | 3.7037 | -107.4074 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 100 | C | 3.5336 | -134.629 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 334 | 352 | 450 | C | 5/8 | 3.6 | 100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 97 | 200 | C | 2.1818 | -5.5455 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 150 | C | 2.1739 | 4.3478 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 352 | 400 | 450 | C | 5/8 | 4 | 72 | 0 | 0 | 0 | 0 | 0 | 0 |  | 97 | 200 | 200 | C | 3.2188 | -54.2812 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 150 | C | 2.7778 | -22.2222 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 360 | 400 | 500 | C | 5/8 | 4.444 | 71.111 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 200 | C | 3.8462 | -103.8462 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 150 | C | 2.8169 | -25.3521 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 117 | 50 | D | 11/16 | 2.68 | -57.2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 200 | C | 3.5714 | -75 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 150 | C | 3.0769 | -55.3846 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 117 | 162 | 50 | D | 11/16 | 3 | -78 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 250 | C | 2.8824 | -9.5294 | 0 | 0 | 0 | 0 | 0 | 0 |  | 65 | 100 | 200 | C | 1.9231 | 28.8462 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 162 | 268 | 50 | D | 11/16 | 3.533 | -120.666 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 250 | C | 2.8571 | -8.5714 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 200 | C | 2.8986 | -7.2464 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 268 | 305 | 50 | D | 11/16 | 4.111 | -184.222 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 250 | C | 3.5714 | -60.7143 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 200 | C | 3.125 | -23.4375 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 305 | 349 | 50 | D | 11/16 | 4 | -171 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 250 | C | 3.7037 | -74.0741 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 200 | C | 3.0769 | -18.4615 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 349 | 400 | 50 | D | 11/16 | 4.25 | -203.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 300 | C | 3.125 | -6.25 | 0 | 0 | 0 | 0 | 0 | 0 |  | 60 | 100 | 250 | C | 3.3333 | -6.6667 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 135 | 100 | D | 11/16 | 2.5 | -27.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 300 | C | 3.4483 | -27.5862 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 250 | C | 3.3333 | -6.6667 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 135 | 183 | 100 | D | 11/16 | 3.2 | -73 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 300 | C | 3.3333 | -16.6667 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 250 | C | 3.0769 | 9.2308 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 183 | 260 | 100 | D | 11/16 | 3.85 | -125 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 350 | C | 3.2258 | 12.9032 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 250 | C | 3.1447 | 2.8302 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 260 | 340 | 100 | D | 11/16 | 4 | -140 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 350 | C | 3.3333 | 6.6667 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99 | 200 | 300 | C | 3.7736 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 340 | 400 | 100 | D | 11/16 | 4.615 | -213.846 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 350 | C | 3.5714 | -14.2857 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 300 | C | 3.3333 | 23.3333 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 162 | 150 | D | 11/16 | 2.872 | -24.667 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 400 | C | 3.3333 | 40 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 300 | C | 3.7037 | -7.4074 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 162 | 246 | 150 | D | 11/16 | 3.36 | -56.4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 400 | C | 3.4483 | 34.4828 | 0 | 0 | 0 | 0 | 0 | 0 |  | 110 | 200 | 350 | C | 2.9851 | 52.2388 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 246 | 284 | 150 | D | 11/16 | 3.8 | -96 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 400 | C | 3.7037 | 14.8148 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 350 | C | 3.8462 | 9.6154 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 284 | 325 | 150 | D | 11/16 | 4.1 | -126 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 450 | C | 3.5714 | 57.1429 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 350 | C | 3.9216 | 3.9216 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 325 | 400 | 150 | D | 11/16 | 4.688 | -190.625 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 450 | C | 4 | 28 | 0 | 0 | 0 | 0 | 0 | 0 |  | 135 | 200 | 400 | C | 2.7027 | 83.7838 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 188 | 236 | 200 | D | 11/16 | 3.2 | -20 | 0 | 0 | 0 | 0 | 0 | 0 |  | 199 | 300 | 500 | C | 3.4483 | 93.1034 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 400 | C | 4 | 28 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 236 | 274 | 200 | D | 11/16 | 3.8 | -68 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 500 | C | 4.1667 | 50 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 400 | C | 4 | 28 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 274 | 347 | 200 | D | 11/16 | 3.65 | -54.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 99 | 50 | D | 1.8889 | -29.4444 | 0 | 0 | 0 | 0 | 0 | 0 |  | 199 | 300 | 450 | C | 3.7736 | 60.3774 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 347 | 400 | 200 | D | 11/16 | 4.417 | -138.833 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99 | 202 | 50 | D | 3.1212 | -113.2424 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 450 | C | 4.717 | 0.4717 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 207 | 297 | 250 | D | 11/16 | 3.6 | -27 | 0 | 0 | 0 | 0 | 0 | 0 |  | 202 | 302 | 50 | D | 3.7037 | -172.0741 | 0 | 0 | 0 | 0 | 0 | 0 |  | 199 | 300 | 500 | C | 3.0769 | 123.0769 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 297 | 334 | 250 | D | 11/16 | 3.7 | -36 | 0 | 0 | 0 | 0 | 0 | 0 |  | 302 | 400 | 50 | D | 4.0833 | -220.6667 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 500 | C | 3.8168 | 80.5344 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 334 | 400 | 250 | D | 11/16 | 4.4 | -106 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 102 | 100 | D | 2.08 | -33.2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 50 | D | 2.1739 | -50 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 230 | 270 | 300 | D | 11/16 | 4 | -30 | 0 | 0 | 0 | 0 | 0 | 0 |  | 102 | 200 | 100 | D | 3.0625 | -97.0625 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 50 | D | 3.0769 | -112.3077 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 270 | 332 | 300 | D | 11/16 | 4.133 | -40 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 301 | 100 | D | 3.7407 | -162.8519 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 50 | D | 3.4483 | -150 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 332 | 400 | 300 | D | 11/16 | 4.857 | -105.143 | 0 | 0 | 0 | 0 | 0 | 0 |  | 301 | 400 | 100 | D | 4.125 | -210.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 50 | D | 4.6838 | -311.2412 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 261 | 330 | 350 | D | 11/16 | 4.6 | -38 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 99 | 150 | D | 2.087 | -22.0435 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 100 | D | 2.381 | -40.4762 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 330 | 400 | 350 | D | 11/16 | 5.385 | -100.769 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99 | 198 | 150 | D | 3 | -75 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 100 | D | 2.7027 | -59.4595 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 260 | 330 | 400 | D | 11/16 | 4.666 | -43.333 | 0 | 0 | 0 | 0 | 0 | 0 |  | 198 | 300 | 150 | D | 3.6429 | -133.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 100 | D | 2.9851 | -86.5672 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 330 | 400 | 400 | D | 11/16 | 5.385 | -100.769 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 150 | D | 3.8462 | -157.6923 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 100 | D | 3.4305 | -144.2539 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 300 | 330 | 450 | D | 11/16 | 3 | 105 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 97 | 200 | D | 1.9167 | -4.5833 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 150 | D | 2.3256 | -16.2791 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 330 | 370 | 450 | D | 11/16 | 4 | 30 | 0 | 0 | 0 | 0 | 0 | 0 |  | 97 | 200 | 200 | D | 3.0294 | -63.5588 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 150 | D | 2.7778 | -38.8889 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 370 | 400 | 450 | D | 11/16 | 5 | -55 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 200 | D | 3.4483 | -100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 150 | D | 2.8369 | -43.9716 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 325 | 360 | 500 | D | 11/16 | 4.375 | 40.625 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 200 | D | 3.7037 | -129.6296 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 150 | D | 3.1496 | -81.8898 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 360 | 400 | 500 | D | 11/16 | 4.444 | 35.555 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 101 | 250 | D | 2 | 5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 50 | 100 | 200 | D | 2.0833 | 9.375 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 100 | 50 | E | 3/4 | 2.5 | -62.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 101 | 198 | 250 | D | 3.0312 | -44.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 200 | D | 2.963 | -28.8889 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 100 | 140 | 50 | E | 3/4 | 2.666 | -73.333 | 0 | 0 | 0 | 0 | 0 | 0 |  | 198 | 299 | 250 | D | 3.2581 | -62.6452 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 200 | D | 3.0769 | -37.6923 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 140 | 240 | 50 | E | 3/4 | 3.448 | -135.862 | 0 | 0 | 0 | 0 | 0 | 0 |  | 299 | 400 | 250 | D | 3.6071 | -101.3929 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 200 | D | 3.1008 | -40.3101 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 240 | 316 | 50 | E | 3/4 | 3.619 | -154.476 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 99 | 300 | D | 2.1739 | 14.2174 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 250 | D | 2.7778 | -5.5556 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 316 | 400 | 50 | E | 3/4 | 3.111 | -88.444 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99 | 198 | 300 | D | 2.9118 | -14.5588 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 250 | D | 3.2787 | -24.5902 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 116 | 100 | E | 3/4 | 2.276 | -31.931 | 0 | 0 | 0 | 0 | 0 | 0 |  | 198 | 297 | 300 | D | 3.3 | -42.9 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 250 | D | 3.1008 | -12.4031 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 116 | 166 | 100 | E | 3/4 | 3.333 | -100.666 | 0 | 0 | 0 | 0 | 0 | 0 |  | 297 | 400 | 300 | D | 3.3226 | -45.2258 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 250 | D | 3.2362 | -26.0518 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 166 | 237 | 100 | E | 3/4 | 3.55 | -118 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 350 | D | 3.1935 | -1.1935 | 0 | 0 | 0 | 0 | 0 | 0 |  | 75 | 100 | 300 | D | 2.0202 | 35.8586 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 237 | 305 | 100 | E | 3/4 | 3.579 | -120.895 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 350 | D | 3.3333 | -10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 300 | D | 3.6036 | -14.4144 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 305 | 350 | 100 | E | 3/4 | 4.09 | -181.81 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 350 | D | 3.2258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 300 | D | 3.3898 | -1.6949 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 350 | 400 | 100 | E | 3/4 | 5 | -300 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 198 | 400 | D | 3.2667 | 28.1333 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 300 | D | 3.7736 | -35.8491 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 135 | 150 | E | 3/4 | 2.576 | -32.424 | 0 | 0 | 0 | 0 | 0 | 0 |  | 198 | 303 | 400 | D | 3.2812 | 27.375 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99 | 200 | 350 | D | 2.8777 | 39.5683 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 135 | 182 | 150 | E | 3/4 | 3.133 | -68.666 | 0 | 0 | 0 | 0 | 0 | 0 |  | 303 | 400 | 400 | D | 3.6071 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 350 | D | 3.9216 | -18.6275 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 182 | 252 | 150 | E | 3/4 | 3.5 | -98 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 284 | 450 | D | 3.32 | 54.92 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 350 | D | 4.0404 | -28.2828 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 252 | 288 | 150 | E | 3/4 | 3.6 | -108 | 0 | 0 | 0 | 0 | 0 | 0 |  | 284 | 400 | 450 | D | 3.8667 | 17.2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 125 | 200 | 400 | D | 2.4096 | 80.7229 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 288 | 327 | 150 | E | 3/4 | 3.9 | -141 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 259 | 500 | D | 3.4706 | 75.0588 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 400 | D | 3.8462 | 9.6154 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 327 | 400 | 150 | E | 3/4 | 4.294 | -188.294 | 0 | 0 | 0 | 0 | 0 | 0 |  | 259 | 400 | 500 | D | 3.9167 | 51.4167 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 400 | D | 4.0816 | -8.1633 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 167 | 180 | 200 | E | 3/4 | 2.6 | -2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 101 | 50 | E | 1.6897 | -27.4138 | 0 | 0 | 0 | 0 | 0 | 0 |  | 130 | 200 | 450 | D | 2.9412 | 73.5294 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 180 | 282 | 200 | E | 3/4 | 3.4 | -58 | 0 | 0 | 0 | 0 | 0 | 0 |  | 101 | 199 | 50 | E | 3.0625 | -131.75 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 450 | D | 4.1237 | 22.6804 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 282 | 320 | 200 | E | 3/4 | 3.8 | -98 | 0 | 0 | 0 | 0 | 0 | 0 |  | 199 | 300 | 50 | E | 3.6071 | -190.5714 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 450 | D | 4.329 | 8.8745 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 320 | 400 | 200 | E | 3/4 | 4 | -120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 50 | E | 4.1667 | -266.6667 | 0 | 0 | 0 | 0 | 0 | 0 |  | 199 | 300 | 500 | D | 3.0534 | 111.4504 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 187 | 200 | 250 | E | 3/4 | 2.6 | 18 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 101 | 100 | E | 1.6333 | -18.2333 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 500 | D | 3.7594 | 67.8571 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 200 | 275 | 250 | E | 3/4 | 3.75 | -62.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 101 | 200 | 100 | E | 3 | -118 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 101 | 50 | E | 1.8889 | -38.7778 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 275 | 353 | 250 | E | 3/4 | 3.9 | -76 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 303 | 100 | E | 3.8148 | -204.3704 | 0 | 0 | 0 | 0 | 0 | 0 |  | 101 | 200 | 50 | E | 2.9118 | -114.4706 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 353 | 400 | 250 | E | 3/4 | 4.7 | -164 | 0 | 0 | 0 | 0 | 0 | 0 |  | 303 | 400 | 100 | E | 3.88 | -213.04 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 302 | 50 | E | 3.6429 | -193.4286 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 200 | 253 | 300 | E | 3/4 | 3.533 | -29.666 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 150 | E | 1.7857 | -16.0714 | 0 | 0 | 0 | 0 | 0 | 0 |  | 302 | 400 | 50 | E | 4.4545 | -303.8182 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 253 | 331 | 300 | E | 3/4 | 3.9 | -59 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 198 | 150 | E | 2.8 | -82 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 100 | E | 2.4286 | -55.4286 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 331 | 400 | 300 | E | 3/4 | 4.929 | -161.857 | 0 | 0 | 0 | 0 | 0 | 0 |  | 198 | 302 | 150 | E | 3.7143 | -173.4286 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 100 | E | 2.6667 | -70.6667 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 230 | 293 | 350 | E | 3/4 | 4.2 | -43 | 0 | 0 | 0 | 0 | 0 | 0 |  | 302 | 400 | 150 | E | 3.7692 | -180.4615 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 100 | E | 2.8986 | -94.2029 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 293 | 400 | 350 | E | 3/4 | 4.458 | -63.666 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 98 | 200 | E | 1.8 | -10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 100 | E | 3.2667 | -144.2667 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 240 | 260 | 400 | E | 3/4 | 4 | -20 | 0 | 0 | 0 | 0 | 0 | 0 |  | 98 | 199 | 200 | E | 2.7297 | -65.7838 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 99 | 150 | E | 2.55 | -43.8 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 260 | 340 | 400 | E | 3/4 | 4.444 | -51.111 | 0 | 0 | 0 | 0 | 0 | 0 |  | 199 | 300 | 200 | E | 3.4828 | -138.8276 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99 | 198 | 150 | E | 2.75 | -55 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 340 | 400 | 400 | E | 3/4 | 5 | -100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 200 | E | 3.8462 | -184.6154 | 0 | 0 | 0 | 0 | 0 | 0 |  | 198 | 301 | 150 | E | 2.9429 | -72.7429 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 253 | 270 | 450 | E | 3/4 | 3.4 | 32 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 99 | 250 | E | 1.7407 | 5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 301 | 400 | 150 | E | 3.1935 | -104.5806 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 270 | 350 | 450 | E | 3/4 | 4 | -10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99 | 198 | 250 | E | 2.9118 | -58.2353 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 101 | 200 | E | 2.4545 | -21.7273 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 350 | 400 | 450 | E | 3/4 | 5 | -100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 198 | 300 | 250 | E | 3.2903 | -91.5484 | 0 | 0 | 0 | 0 | 0 | 0 |  | 101 | 199 | 200 | E | 2.9697 | -47.4848 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 278 | 320 | 500 | E | 3/4 | 4.2 | 5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 250 | E | 3.5714 | -125 | 0 | 0 | 0 | 0 | 0 | 0 |  | 199 | 298 | 200 | E | 3 | -50 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 320 | 400 | 500 | E | 3/4 | 5 | -55 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 103 | 300 | E | 1.8276 | 15.2759 | 0 | 0 | 0 | 0 | 0 | 0 |  | 298 | 400 | 200 | E | 3.1875 | -71.75 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 85 | 50 | F | 13/16 | 1.944 | -41.389 | 0 | 0 | 0 | 0 | 0 | 0 |  | 103 | 202 | 300 | E | 3 | -41 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 99 | 250 | E | 2.2857 | -1.5714 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 85 | 119 | 50 | F | 13/16 | 2.429 | -72.857 | 0 | 0 | 0 | 0 | 0 | 0 |  | 202 | 298 | 300 | E | 3.2 | -57.2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99 | 201 | 250 | E | 3.2903 | -45.7742 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 119 | 133 | 50 | F | 13/16 | 2.8 | -102.2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 298 | 400 | 300 | E | 3.2903 | -67.2258 | 0 | 0 | 0 | 0 | 0 | 0 |  | 201 | 302 | 250 | E | 3.1562 | -35.7188 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 133 | 213 | 50 | F | 13/16 | 3.2 | -135.8 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 197 | 350 | E | 3.2333 | -22.8667 | 0 | 0 | 0 | 0 | 0 | 0 |  | 302 | 400 | 250 | E | 3.2667 | -47.5333 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 213 | 250 | 50 | F | 13/16 | 3.363 | -153.636 | 0 | 0 | 0 | 0 | 0 | 0 |  | 197 | 301 | 350 | E | 3.1515 | -17.303 | 0 | 0 | 0 | 0 | 0 | 0 |  | 60 | 99 | 300 | E | 2.1739 | 18.5652 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 250 | 280 | 50 | F | 13/16 | 3 | -110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 301 | 400 | 350 | E | 3.3846 | -40.8462 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99 | 201 | 300 | E | 3.5172 | -31.1379 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 280 | 400 | 50 | F | 13/16 | 4 | -240 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 201 | 400 | E | 3.1562 | 11.625 | 0 | 0 | 0 | 0 | 0 | 0 |  | 201 | 300 | 300 | E | 3.4138 | -24.3103 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 103 | 100 | F | 13/16 | 2.304 | -46.783 | 0 | 0 | 0 | 0 | 0 | 0 |  | 201 | 303 | 400 | E | 3.2903 | 3.5806 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 300 | E | 3.8462 | -65.3846 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 103 | 175 | 100 | F | 13/16 | 2.88 | -84.2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 303 | 400 | 400 | E | 3.7308 | -36.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 98 | 200 | 350 | E | 2.8333 | 24.3333 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 175 | 205 | 100 | F | 13/16 | 3.333 | -125 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 197 | 450 | E | 3.2 | 37 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 298 | 350 | E | 3.92 | -43.04 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 205 | 242 | 100 | F | 13/16 | 3.7 | -161.3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 197 | 287 | 450 | E | 3.3333 | 30.3333 | 0 | 0 | 0 | 0 | 0 | 0 |  | 298 | 400 | 350 | E | 4.25 | -71.75 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 242 | 317 | 100 | F | 13/16 | 3.409 | -129.59 | 0 | 0 | 0 | 0 | 0 | 0 |  | 287 | 400 | 450 | E | 3.7667 | -3.0333 | 0 | 0 | 0 | 0 | 0 | 0 |  | 120 | 200 | 400 | E | 2.1522 | 79.4783 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 317 | 355 | 100 | F | 13/16 | 4.222 | -236.111 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 259 | 500 | E | 3.6875 | 37.75 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 400 | E | 3.7037 | -7.4074 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 355 | 400 | 100 | F | 13/16 | 4.5 | -275 | 0 | 0 | 0 | 0 | 0 | 0 |  | 259 | 400 | 500 | E | 3.9167 | 24 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 400 | E | 4.1667 | -45.8333 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 115 | 150 | F | 13/16 | 2.321 | -35.893 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 50 | F | 1.3421 | -11.3947 | 0 | 0 | 0 | 0 | 0 | 0 |  | 119 | 202 | 450 | E | 2.6774 | 70.8065 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 115 | 160 | 150 | F | 13/16 | 3 | -80 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 50 | F | 3.0303 | -151.5152 | 0 | 0 | 0 | 0 | 0 | 0 |  | 202 | 285 | 450 | E | 3.7727 | 17.1364 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 160 | 223 | 150 | F | 13/16 | 3.15 | -92 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 303 | 50 | F | 3.9615 | -259.5385 | 0 | 0 | 0 | 0 | 0 | 0 |  | 285 | 400 | 450 | E | 4.6 | -41.6 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 223 | 334 | 150 | F | 13/16 | 3.7 | -147 | 0 | 0 | 0 | 0 | 0 | 0 |  | 303 | 400 | 50 | F | 3.7308 | -226.7692 | 0 | 0 | 0 | 0 | 0 | 0 |  | 199 | 254 | 500 | E | 2.8947 | 103.4737 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 334 | 400 | 150 | F | 13/16 | 4.1245 | -202.25 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 100 | F | 1.4444 | -12.6667 | 0 | 0 | 0 | 0 | 0 | 0 |  | 254 | 300 | 500 | E | 3.2857 | 83.1429 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 143 | 200 | F | 13/16 | 2.818 | -40.182 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 199 | 100 | F | 2.9118 | -127.1176 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 500 | E | 3.7037 | 55.5556 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 143 | 188 | 200 | F | 13/16 | 3 | -52 | 0 | 0 | 0 | 0 | 0 | 0 |  | 199 | 303 | 100 | F | 3.8519 | -232.4074 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 50 | F | 1.6129 | -26.6129 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 188 | 250 | 200 | F | 13/16 | 3.1 | -60 | 0 | 0 | 0 | 0 | 0 | 0 |  | 303 | 400 | 100 | F | 3.7308 | -215.5769 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 50 | F | 2.7397 | -115.0685 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 250 | 320 | 200 | F | 13/16 | 3.5 | -100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 99 | 150 | F | 1.5625 | -11.9375 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 50 | F | 3.7037 | -225.9259 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 320 | 400 | 200 | F | 13/16 | 4 | -160 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99 | 197 | 150 | F | 2.8 | -99.8 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 50 | F | 4.3478 | -317.3913 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 160 | 173 | 250 | F | 13/16 | 2.6 | -9 | 0 | 0 | 0 | 0 | 0 | 0 |  | 197 | 301 | 150 | F | 3.5862 | -183.1379 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 100 | F | 2.0619 | -43.8144 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 173 | 204 | 250 | F | 13/16 | 3.444 | -68.111 | 0 | 0 | 0 | 0 | 0 | 0 |  | 301 | 400 | 150 | F | 3.8077 | -213.0385 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 100 | F | 2.6846 | -87.2483 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 204 | 260 | 250 | F | 13/16 | 3.111 | -41.777 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 99 | 200 | F | 1.6552 | -8.5862 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 100 | F | 2.7972 | -99.3007 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 260 | 308 | 250 | F | 13/16 | 3.692 | -98.154 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99 | 201 | 200 | F | 2.6842 | -75.4737 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 100 | F | 3.4188 | -188.0342 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 308 | 347 | 250 | F | 13/16 | 3.9 | -121 | 0 | 0 | 0 | 0 | 0 | 0 |  | 201 | 303 | 200 | F | 3.5172 | -161.2759 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 150 | F | 1.9608 | -22.549 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 347 | 400 | 250 | F | 13/16 | 4.416 | -183 | 0 | 0 | 0 | 0 | 0 | 0 |  | 303 | 400 | 200 | F | 3.5463 | -165.1147 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 150 | F | 2.7778 | -73.6111 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 177 | 261 | 300 | F | 13/16 | 3.5 | -50.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 250 | F | 1.6129 | 3.2258 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 150 | F | 2.8777 | -83.4532 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 261 | 300 | 300 | F | 13/16 | 3.545 | -54.545 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 199 | 250 | F | 2.8286 | -69.7143 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 150 | F | 3.252 | -133.3333 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 300 | 346 | 300 | F | 13/16 | 4.6 | -160 | 0 | 0 | 0 | 0 | 0 | 0 |  | 199 | 296 | 250 | F | 3.3448 | -118.7586 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 200 | F | 1.9802 | -11.3861 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 346 | 400 | 300 | F | 13/16 | 4.909 | -194 | 0 | 0 | 0 | 0 | 0 | 0 |  | 296 | 400 | 250 | F | 3.4667 | -133.8667 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 200 | F | 2.9412 | -65.4412 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 209 | 260 | 350 | F | 13/16 | 3.4 | -12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 99 | 300 | F | 1.7241 | 9.3448 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 200 | F | 3.0534 | -75.5725 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 260 | 340 | 350 | F | 13/16 | 4 | -60 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99 | 200 | 300 | F | 2.8857 | -51.0571 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 200 | F | 3.125 | -84.375 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 340 | 400 | 350 | F | 13/16 | 4.615 | -121.538 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 301 | 300 | F | 3.3667 | -92.9 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 250 | F | 1.9608 | 2.9412 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 217 | 273 | 400 | F | 13/16 | 3.733 | -25.666 | 0 | 0 | 0 | 0 | 0 | 0 |  | 301 | 400 | 300 | F | 3.2632 | -80.7895 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 250 | F | 3.1496 | -55.9055 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 273 | 354 | 400 | F | 13/16 | 4.05 | -51 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 350 | F | 1.75 | 23 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 250 | F | 3.1008 | -51.938 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 354 | 400 | 400 | F | 13/16 | 4.6 | -106 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 201 | 350 | F | 3.0606 | -34.6667 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 250 | F | 3.1746 | -60.3175 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 240 | 295 | 450 | F | 13/16 | 3.666 | 1.666 | 0 | 0 | 0 | 0 | 0 | 0 |  | 201 | 299 | 350 | F | 3.2667 | -50.5333 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 300 | F | 2.6316 | -13.1579 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 295 | 360 | 450 | F | 13/16 | 4.333 | -51.666 | 0 | 0 | 0 | 0 | 0 | 0 |  | 299 | 400 | 350 | F | 3.6364 | -90.0909 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 300 | F | 3.2787 | -40.9836 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 360 | 400 | 450 | F | 13/16 | 5 | -115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 97 | 198 | 400 | F | 2.8056 | 7.2222 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 300 | F | 3.4783 | -55.6522 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 258 | 350 | 500 | F | 13/16 | 4.6 | -41 | 0 | 0 | 0 | 0 | 0 | 0 |  | 198 | 298 | 400 | F | 3.3333 | -28.6667 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 300 | F | 3.6036 | -68.4685 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 350 | 400 | 500 | F | 13/16 | 6.25 | -181.25 | 0 | 0 | 0 | 0 | 0 | 0 |  | 298 | 400 | 400 | F | 3.7778 | -72.2222 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99 | 200 | 350 | F | 2.8986 | 0.72464 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 83 | 50 | G | 7/8 | 1.833 | -36.167 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 450 | F | 3.0938 | 11.2812 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 350 | F | 4.0816 | -80.6122 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 83 | 110 | 50 | G | 7/8 | 1.8 | -34 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 288 | 450 | F | 3.52 | -14.72 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 350 | F | 4.2105 | -92.6316 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 110 | 135 | 50 | G | 7/8 | 2.5 | -90 | 0 | 0 | 0 | 0 | 0 | 0 |  | 288 | 400 | 450 | F | 3.3488 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 110 | 200 | 400 | F | 2.0202 | 73.7374 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 135 | 195 | 50 | G | 7/8 | 3 | -135 | 0 | 0 | 0 | 0 | 0 | 0 |  | 196 | 256 | 500 | F | 3.75 | -2.75 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 400 | F | 3.5088 | -19.2982 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 195 | 365 | 50 | G | 7/8 | 3.5417 | -194.58 | 0 | 0 | 0 | 0 | 0 | 0 |  | 256 | 400 | 500 | F | 4 | -20 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 400 | F | 4.1667 | -79.1667 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 93 | 100 | G | 7/8 | 1.955 | -34.045 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 50 | G | 1.1136 | -1.3409 | 0 | 0 | 0 | 0 | 0 | 0 |  | 105 | 200 | 450 | F | 2.4691 | 60.4938 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 93 | 130 | 100 | G | 7/8 | 2.466 | -67.333 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 50 | G | 3.2258 | -193.5484 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 450 | F | 3.9216 | -21.5686 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 130 | 190 | 100 | G | 7/8 | 3 | -110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 50 | G | 3.8462 | -269.2308 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 450 | F | 4.5455 | -72.7273 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 190 | 253 | 100 | G | 7/8 | 3.15 | -125 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 365 | 50 | G | 3.9359 | -282.5162 | 0 | 0 | 0 | 0 | 0 | 0 |  | 115 | 200 | 500 | F | 4.3478 | 30.4348 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 253 | 300 | 100 | G | 7/8 | 3.357 | -149.86 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 100 | G | 1.3158 | -7.8947 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 500 | F | 3.2258 | 74.1935 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 300 | 365 | 100 | G | 7/8 | 3.8235 | -212.35 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 100 | G | 2.7027 | -121.6216 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 400 | 500 | F | 3.7037 | 40.7407 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 101 | 150 | G | 7/8 | 1.889 | -21.778 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 100 | G | 4 | -276 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 50 | G | 1.4286 | -18.5714 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 101 | 140 | 150 | G | 7/8 | 2.6 | -68 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 365 | 100 | G | 3.8235 | -250.5882 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 50 | G | 2.5641 | -112.8205 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 140 | 265 | 150 | G | 7/8 | 3.125 | -110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 150 | G | 1.3333 | -4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 50 | G | 3.8462 | -269.2308 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 265 | 300 | 150 | G | 7/8 | 3.181 | -116.818 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 150 | G | 2.8571 | -122.8571 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 365 | 50 | G | 4.0625 | -301.25 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 300 | 336 | 150 | G | 7/8 | 4 | -224 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 150 | G | 3.7037 | -218.5185 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 100 | G | 1.8182 | -37.2727 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 336 | 365 | 150 | G | 7/8 | 4.143 | -244 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 365 | 150 | G | 3.6111 | -205.5556 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 100 | G | 2.7027 | -104.0541 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 123 | 200 | G | 7/8 | 2.355 | -30.065 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 200 | G | 1.4848 | -5.4242 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 100 | G | 2.7027 | -104.0541 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 123 | 135 | 200 | G | 7/8 | 2.4 | -33 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 200 | G | 2.8571 | -102.8571 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 365 | 100 | G | 3.1707 | -174.0244 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 135 | 160 | 200 | G | 7/8 | 2.5 | -40 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 200 | G | 3.4483 | -165.5172 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 150 | G | 1.6129 | -11.2903 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 160 | 253 | 200 | G | 7/8 | 3.1 | -88 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 365 | 200 | G | 3.6111 | -187.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 150 | G | 2.7778 | -91.6667 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 253 | 320 | 200 | G | 7/8 | 3.35 | -115.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 250 | G | 1.6667 | -3.3333 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 150 | G | 2.8986 | -104.3478 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 320 | 365 | 200 | G | 7/8 | 3.462 | -130 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 250 | G | 2.6316 | -63.1579 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 365 | 150 | G | 3.0233 | -121.7442 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 134 | 250 | G | 7/8 | 2.333 | -17.667 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 250 | G | 3.4483 | -144.8276 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 200 | G | 1.7544 | -9.6491 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 134 | 176 | 250 | G | 7/8 | 2.8 | -48 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 300 | 365 | 250 | G | 3.25 | -119.25 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 200 | G | 2.8571 | -78.5714 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 176 | 240 | 250 | G | 7/8 | 3.2 | -80 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 300 | G | 1.6552 | 5.6552 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 200 | G | 3.0769 | -100 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 240 | 303 | 250 | G | 7/8 | 3.316 | -91.579 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 300 | G | 2.7778 | -58.3333 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 365 | 200 | G | 3.0952 | -102.381 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 303 | 342 | 250 | G | 7/8 | 3.9 | -161.1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 300 | G | 3.4483 | -120.6897 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 250 | G | 1.6667 | 8.3333 | 0 | 0 | 0 | 0 | 0 | 0
[21 empty] | 400 | 342 | 365 | 250 | G | 7/8 | 3.833 | -152.5 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 300 | 365 | 300 | G | 3.4211 | -117.3684 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 250 | G | 3.0769 | -69.2308 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 156 | 240 | 300 | G | 7/8 | 3.36 | -62.4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 350 | G | 1.5714 | 19.8571 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 250 | G | 3.0769 | -69.2308 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 240 | 320 | 300 | G | 7/8 | 3.81 | -102.857 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 350 | G | 2.9412 | -50 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 300 | 365 | 250 | G | 3.25 | -90 | 0 | 0 | 0 | 0 | 0 | 0
[21 empty] | 400 | 320 | 365 | 300 | G | 7/8 | 5 | -235 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 350 | G | 3.4483 | -93.1034 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 300 | G | 1.9231 | 5.7692 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 184 | 262 | 350 | G | 7/8 | 3.25 | -27.25 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 365 | 350 | G | 3.25 | -70.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 300 | G | 3.125 | -53.125 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 262 | 300 | 350 | G | 7/8 | 3.454 | -45.454 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 400 | G | 2.9412 | -26.4706 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 300 | G | 3.5088 | -84.2105 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 300 | 365 | 350 | G | 7/8 | 4.0625 | -106.25 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 400 | G | 3.5714 | -75 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 300 | 365 | 300 | G | 3.7143 | -106.7143 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 200 | 250 | 400 | G | 7/8 | 3.333 | -16.666 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 365 | 400 | G | 3.6111 | -79.1667 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99 | 200 | 350 | G | 3.0303 | -28.7879 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 250 | 327 | 400 | G | 7/8 | 3.85 | -58 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 450 | G | 3.0303 | -12.1212 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 350 | G | 4.1667 | -114.5833 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 327 | 365 | 400 | G | 7/8 | 4.222 | -95.222 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 450 | G | 3.5714 | -50 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 365 | 350 | G | 4.4828 | -146.0345 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 227 | 243 | 450 | G | 7/8 | 4 | -33 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 365 | 450 | G | 3.0952 | -3.3333 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 400 | G | 1.8868 | 69.8113 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 243 | 365 | 450 | G | 7/8 | 4.067 | -37.6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 500 | G | 2.5641 | 41.0256 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 400 | G | 3.3333 | -30 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 237 | 258 | 500 | G | 7/8 | 3.5 | 9.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 500 | G | 3.7037 | -29.6296 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 365 | 400 | G | 4.3333 | -129 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 258 | 355 | 500 | G | 7/8 | 4.85 | -86.35 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 365 | 500 | G | 3.9375 | -50.4401 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 450 | G | 2.1739 | 60.8696 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 355 | 365 | 500 | G | 7/8 | 5 | -100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 99 | 50 | H | 1.1111 | -2.1111 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 450 | G | 3.7736 | -41.5094 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 75 | 50 | H | 15/16 | 1.389 | -15.278 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99 | 203 | 50 | H | 2.6 | -137.6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 365 | 450 | G | 4.4828 | -105.6897 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 75 | 97 | 50 | H | 15/16 | 1.466 | -20.333 | 0 | 0 | 0 | 0 | 0 | 0 |  | 203 | 300 | 50 | H | 3.5926 | -267.6296 | 0 | 0 | 0 | 0 | 0 | 0 |  | 120 | 200 | 500 | G | 3.0303 | 63.6364 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 97 | 117 | 50 | H | 15/16 | 2 | -63 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 340 | 50 | H | 4 | -332 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 500 | G | 3.3333 | 50 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 117 | 268 | 50 | H | 15/16 | 3.02 | -154.8 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 99 | 100 | H | 1.1364 | -1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 365 | 500 | G | 3.8235 | 13.2353 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 268 | 300 | 50 | H | 15/16 | 4 | -292 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99 | 205 | 100 | H | 2.65 | -134.2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 50 | H | 1.1905 | -7.7381 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 300 | 339 | 50 | H | 15/16 | 3.25 | -181 | 0 | 0 | 0 | 0 | 0 | 0 |  | 205 | 294 | 100 | H | 3.7083 | -269.6667 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 50 | H | 2.5641 | -132.0513 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 80 | 100 | H | 15/16 | 1.429 | -12.857 | 0 | 0 | 0 | 0 | 0 | 0 |  | 294 | 340 | 100 | H | 3.8333 | -288.6667 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 50 | H | 3.6036 | -266.6667 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 80 | 100 | 100 | H | 15/16 | 1.666 | -28.333 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 98 | 150 | H | 1.2632 | -3.0526 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 340 | 50 | H | 3.9024 | -313.6585 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 100 | 120 | 100 | H | 15/16 | 2.222 | -71.111 | 0 | 0 | 0 | 0 | 0 | 0 |  | 98 | 198 | 150 | H | 2.5 | -102 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 100 | H | 1.4388 | -16.9065 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 120 | 160 | 100 | H | 15/16 | 2.857 | -125.714 | 0 | 0 | 0 | 0 | 0 | 0 |  | 198 | 300 | 150 | H | 3.5172 | -224.069 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 100 | H | 2.5641 | -108.3333 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 160 | 222 | 100 | H | 15/16 | 3.263 | -166.32 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 340 | 150 | H | 4 | -296 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 100 | H | 2.8571 | -143.5714 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 222 | 339 | 100 | H | 15/16 | 3.343 | -175.8 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 101 | 200 | H | 1.3421 | -1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 340 | 100 | H | 3.2653 | -206.9388 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 94 | 150 | H | 15/16 | 1.692 | -16 | 0 | 0 | 0 | 0 | 0 | 0 |  | 101 | 200 | 200 | H | 2.6053 | -97 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 150 | H | 1.4085 | -4.9296 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 94 | 101 | 150 | H | 15/16 | 1.4 | 3 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 303 | 200 | H | 3.3226 | -178.7742 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 150 | H | 2.6316 | -96.0526 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 101 | 125 | 150 | H | 15/16 | 2.4 | -67 | 0 | 0 | 0 | 0 | 0 | 0 |  | 303 | 340 | 200 | H | 3.7 | -233.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 150 | H | 2.963 | -133.3333 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 125 | 180 | 150 | H | 15/16 | 2.619 | -84.524 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 99 | 250 | H | 1.5312 | -3.5938 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 340 | 150 | H | 2.9091 | -125.4545 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 180 | 267 | 150 | H | 15/16 | 3 | -123 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99 | 198 | 250 | H | 2.4146 | -62.7805 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 200 | H | 1.6 | -7.6 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 267 | 339 | 150 | H | 15/16 | 3.429 | -178.71 | 0 | 0 | 0 | 0 | 0 | 0 |  | 198 | 297 | 250 | H | 3.4138 | -170.6897 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 200 | H | 2.7397 | -84.2466 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 100 | 200 | H | 15/16 | 1.667 | -8.333 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 297 | 340 | 250 | H | 3.3077 | -156.1538 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 200 | H | 3.0075 | -112.0301 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 100 | 120 | 200 | H | 15/16 | 2.5 | -62.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 95 | 300 | H | 1.5714 | 3.8571 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 340 | 200 | H | 3.0769 | -121.5385 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 120 | 140 | 200 | H | 15/16 | 2.857 | -88.571 | 0 | 0 | 0 | 0 | 0 | 0 |  | 95 | 204 | 300 | H | 2.4773 | -48.6818 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 250 | H | 1.4925 | 11.194 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 140 | 198 | 200 | H | 15/16 | 2.9 | -92 | 0 | 0 | 0 | 0 | 0 | 0 |  | 204 | 302 | 300 | H | 3.5 | -153 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 250 | H | 2.8369 | -68.7943 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 198 | 292 | 200 | H | 15/16 | 3.133 | -115.333 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 302 | 340 | 300 | H | 3.4545 | -147.0909 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 250 | H | 3.2 | -103.2 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 292 | 339 | 200 | H | 15/16 | 3.357 | -144.43 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 106 | 350 | H | 1.6571 | 14.8571 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 300 | 340 | 250 | H | 3.0769 | -87.6923 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 112 | 250 | H | 15/16 | 1.771 | -3.143 | 0 | 0 | 0 | 0 | 0 | 0 |  | 106 | 200 | 350 | H | 2.5405 | -33.7297 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 300 | H | 1.6949 | 12.7119 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 112 | 127 | 250 | H | 15/16 | 3 | -83 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 298 | 350 | H | 3.1613 | -90.8387 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 300 | H | 2.7778 | -43.0556 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 127 | 180 | 250 | H | 15/16 | 2.65 | -58.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 298 | 340 | 350 | H | 3.5 | -132.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 300 | H | 3.5398 | -109.7345 | 0 | 0 | 0 | 0 | 0 | 0
[21 empty] | 400 | 180 | 340 | 250 | H | 15/16 | 3.3125 | -118.13 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 101 | 400 | H | 1.7778 | 21 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 300 | 340 | 300 | H | 3.5556 | -111.5556 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 132 | 160 | 300 | H | 15/16 | 2.8 | -50 | 0 | 0 | 0 | 0 | 0 | 0 |  | 101 | 195 | 400 | H | 2.6111 | -16.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 65 | 100 | 350 | H | 1.2739 | 42.9936 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 160 | 235 | 300 | H | 15/16 | 3 | -65 | 0 | 0 | 0 | 0 | 0 | 0 |  | 195 | 294 | 400 | H | 3.0938 | -55.5938 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 350 | H | 2.7397 | -22.6027 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 235 | 270 | 300 | H | 15/16 | 3.5 | -115 | 0 | 0 | 0 | 0 | 0 | 0 |  | 294 | 340 | 400 | H | 3.2857 | -77.2857 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 350 | H | 4.1667 | -138.5417 | 0 | 0 | 0 | 0 | 0 | 0
[21 empty] | 400 | 270 | 340 | 300 | H | 15/16 | 4.059 | -176.47 | 0 | 0 | 0 | 0 | 0 | 0 |  | 98 | 201 | 450 | H | 2.641 | -2.359 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 340 | 350 | H | 4.5714 | -181.1429 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 158 | 240 | 350 | H | 15/16 | 3.416 | -64.083 | 0 | 0 | 0 | 0 | 0 | 0 |  | 201 | 287 | 450 | H | 3.1852 | -44.2593 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99 | 200 | 400 | H | 1.8868 | 55.6604 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 240 | 278 | 350 | H | 15/16 | 3.454 | -67.454 | 0 | 0 | 0 | 0 | 0 | 0 |  | 287 | 340 | 450 | H | 3.3125 | -57.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 400 | H | 3.5088 | -68.4211 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 278 | 339 | 350 | H | 15/16 | 4.067 | -128.67 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 197 | 500 | H | 2.6944 | 16.4722 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 340 | 400 | H | 4 | -120 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 188 | 237 | 400 | H | 15/16 | 3.266 | -24.333 | 0 | 0 | 0 | 0 | 0 | 0 |  | 197 | 258 | 500 | H | 3.2105 | -18.1053 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 450 | H | 2 | 64 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 237 | 339 | 400 | H | 15/16 | 3.643 | -54.429 | 0 | 0 | 0 | 0 | 0 | 0 |  | 258 | 340 | 500 | H | 3.28 | -24.08 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 450 | H | 3.7037 | -51.8519 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 185 | 200 | 450 | H | 15/16 | 3 | -10 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 107 | 50 | I | 1.1633 | -7 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 340 | 450 | H | 5 | -175 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 200 | 339 | 450 | H | 15/16 | 3.757 | -62.973 | 0 | 0 | 0 | 0 | 0 | 0 |  | 107 | 205 | 50 | I | 2.3902 | -127.2439 | 0 | 0 | 0 | 0 | 0 | 0 |  | 120 | 200 | 500 | H | 2.5316 | 69.6203 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 208 | 250 | 500 | H | 15/16 | 4.2 | -65 | 0 | 0 | 0 | 0 | 0 | 0 |  | 205 | 287 | 50 | I | 3.7273 | -313.0909 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 500 | H | 3.3898 | 25.4237 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 250 | 320 | 500 | H | 15/16 | 4.666 | -100 | 0 | 0 | 0 | 0 | 0 | 0 |  | 287 | 330 | 50 | I | 3.875 | -336.875 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 340 | 500 | H | 3.6364 | 5.4545 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 320 | 339 | 500 | H | 15/16 | 4.75 | -107.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 107 | 100 | I | 1.2128 | -7 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 104 | 50 | I | 1.102 | -4 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 70 | 50 | I | 1 | 1.111 | -2.222 | 0 | 0 | 0 | 0 | 0 | 0 |  | 107 | 205 | 100 | I | 2.3333 | -112.3333 | 0 | 0 | 0 | 0 | 0 | 0 |  | 104 | 203 | 50 | I | 2.5385 | -144.7692 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 70 | 95 | 50 | I | 1 | 1.316 | -15.526 | 0 | 0 | 0 | 0 | 0 | 0 |  | 205 | 302 | 100 | I | 3.7308 | -302.3846 | 0 | 0 | 0 | 0 | 0 | 0 |  | 203 | 303 | 50 | I | 3.3898 | -261.4068 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 95 | 105 | 50 | I | 1 | 1.666 | -45 | 0 | 0 | 0 | 0 | 0 | 0 |  | 302 | 330 | 100 | I | 3.7692 | -308.6154 | 0 | 0 | 0 | 0 | 0 | 0 |  | 303 | 330 | 50 | I | 4.1538 | -388.6154 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 105 | 120 | 50 | I | 1 | 2.143 | -87.857 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 105 | 150 | I | 1.2727 | -7 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 103 | 100 | I | 1.3095 | -10.9286 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 120 | 185 | 50 | I | 1 | 2.826 | -154.13 | 0 | 0 | 0 | 0 | 0 | 0 |  | 105 | 203 | 150 | I | 2.3333 | -100.3333 | 0 | 0 | 0 | 0 | 0 | 0 |  | 103 | 204 | 100 | I | 2.4634 | -111.3171 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 185 | 243 | 50 | I | 1 | 2.9 | -163 | 0 | 0 | 0 | 0 | 0 | 0 |  | 203 | 301 | 150 | I | 3.6296 | -268.8519 | 0 | 0 | 0 | 0 | 0 | 0 |  | 204 | 302 | 100 | I | 2.9697 | -176.1212 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 243 | 330 | 50 | I | 1 | 3.2222 | -208.11 | 0 | 0 | 0 | 0 | 0 | 0 |  | 301 | 330 | 150 | I | 3.8462 | -302.8462 | 0 | 0 | 0 | 0 | 0 | 0 |  | 302 | 330 | 100 | I | 3.1111 | -198.8889 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 76 | 100 | I | 1 | 1.238 | -4.476 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 103 | 200 | I | 1.3158 | -3.5789 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 103 | 150 | I | 1.4 | -9 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 76 | 95 | 100 | I | 1 | 1.583 | -26.917 | 0 | 0 | 0 | 0 | 0 | 0 |  | 103 | 201 | 200 | I | 2.3333 | -86 | 0 | 0 | 0 | 0 | 0 | 0 |  | 103 | 202 | 150 | I | 2.475 | -95 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 95 | 120 | 100 | I | 1 | 1.667 | -33.333 | 0 | 0 | 0 | 0 | 0 | 0 |  | 201 | 301 | 200 | I | 3.3333 | -209 | 0 | 0 | 0 | 0 | 0 | 0 |  | 202 | 301 | 150 | I | 3 | -158 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 120 | 197 | 100 | I | 1 | 2.75 | -133 | 0 | 0 | 0 | 0 | 0 | 0 |  | 301 | 330 | 200 | I | 3.2222 | -192 | 0 | 0 | 0 | 0 | 0 | 0 |  | 301 | 330 | 150 | I | 2.6364 | -102.3636 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 197 | 220 | 100 | I | 1 | 2.875 | -148 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 101 | 250 | I | 1.4167 | -2.4167 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 103 | 200 | I | 1.5294 | -7.1176 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 220 | 330 | 100 | I | 1 | 3.045 | -169.88 | 0 | 0 | 0 | 0 | 0 | 0 |  | 101 | 199 | 250 | I | 2.2791 | -65.3721 | 0 | 0 | 0 | 0 | 0 | 0 |  | 103 | 202 | 200 | I | 2.6053 | -84.5789 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 85 | 150 | I | 1 | 1.346 | -2.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 199 | 295 | 250 | I | 3.3103 | -185 | 0 | 0 | 0 | 0 | 0 | 0 |  | 202 | 298 | 200 | I | 2.8235 | -108.5882 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 85 | 100 | 150 | I | 1 | 1.363 | -3.6364 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 295 | 330 | 250 | I | 3.1875 | -167.1875 | 0 | 0 | 0 | 0 | 0 | 0 |  | 298 | 330 | 200 | I | 2.9091 | -120.9091 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 100 | 120 | 150 | I | 1 | 2.222 | -68.888 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 300 | I | 1.4857 | 4.9143 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 101 | 250 | I | 1.4324 | 9.3243 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 120 | 180 | 150 | I | 1 | 2.609 | -101.739 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 204 | 300 | I | 2.3111 | -47.9111 | 0 | 0 | 0 | 0 | 0 | 0 |  | 101 | 200 | 250 | I | 2.6053 | -65.7368 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 180 | 270 | 150 | I | 1 | 2.813 | -123.75 | 0 | 0 | 0 | 0 | 0 | 0 |  | 204 | 305 | 300 | I | 3.2581 | -151.129 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 296 | 250 | I | 3.2 | -126.4 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 270 | 330 | 150 | I | 1 | 3 | -150 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 305 | 330 | 300 | I | 3.5714 | -195 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 296 | 330 | 250 | I | 3.0909 | -112 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 92 | 200 | I | 1 | 1.448 | -2.138 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 107 | 350 | I | 1.6364 | 10.4545 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 300 | I | 1.4545 | 21.4545 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 92 | 108 | 200 | I | 1 | 1.777 | -23.555 | 0 | 0 | 0 | 0 | 0 | 0 |  | 107 | 202 | 350 | I | 2.375 | -33.125 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 300 | I | 2.5 | -35 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 108 | 123 | 200 | I | 1 | 2.5 | -77 | 0 | 0 | 0 | 0 | 0 | 0 |  | 202 | 299 | 350 | I | 3.129 | -107.7742 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 302 | 300 | I | 3.6429 | -142.4286 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 123 | 210 | 200 | I | 1 | 2.9 | -109 | 0 | 0 | 0 | 0 | 0 | 0 |  | 299 | 330 | 350 | I | 3.4167 | -145.1667 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 302 | 330 | 300 | I | 3.5 | -125 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 210 | 240 | 200 | I | 1 | 3 | -120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 101 | 400 | I | 1.625 | 21.375 | 0 | 0 | 0 | 0 | 0 | 0 |  | 60 | 104 | 350 | I | 1.5 | 33.5 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 240 | 330 | 200 | I | 1 | 3 | -120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 101 | 197 | 400 | I | 2.4615 | -19.6154 | 0 | 0 | 0 | 0 | 0 | 0 |  | 104 | 200 | 350 | I | 2.4 | -8.8 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 100 | 250 | I | 1 | 1.429 | 7.143 | 0 | 0 | 0 | 0 | 0 | 0 |  | 197 | 302 | 400 | I | 3 | -67 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 350 | I | 4.1667 | -162.5 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 100 | 134 | 250 | I | 1 | 2.266 | -47.333 | 0 | 0 | 0 | 0 | 0 | 0 |  | 302 | 330 | 400 | I | 2.8 | -42.4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 300 | 330 | 350 | I | 4.2857 | -175.7143 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 134 | 194 | 250 | I | 1 | 3 | -106 | 0 | 0 | 0 | 0 | 0 | 0 |  | 98 | 207 | 450 | I | 2.4773 | -1.0909 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99 | 202 | 400 | I | 1.9623 | 37.1698 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 194 | 256 | 250 | I | 1 | 3.1 | -116 | 0 | 0 | 0 | 0 | 0 | 0 |  | 207 | 284 | 450 | I | 2.9615 | -41.7692 | 0 | 0 | 0 | 0 | 0 | 0 |  | 202 | 299 | 400 | I | 3.5926 | -99.7778 | 0 | 0 | 0 | 0 | 0 | 0
[21 empty] | 400 | 256 | 330 | 250 | I | 1 | 3.7 | -188 | 0 | 0 | 0 | 0 | 0 | 0 |  | 284 | 330 | 450 | I | 2.875 | -32.25 | 0 | 0 | 0 | 0 | 0 | 0 |  | 299 | 330 | 400 | I | 3.875 | -131.125 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 112 | 300 | I | 1 | 1.512 | 13.707 | 0 | 0 | 0 | 0 | 0 | 0 |  | 96 | 202 | 500 | I | 2.5238 | 15.2381 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99 | 199 | 450 | I | 1.8519 | 65.6667 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 112 | 180 | 300 | I | 1 | 2.72 | -64.8 | 0 | 0 | 0 | 0 | 0 | 0 |  | 202 | 255 | 500 | I | 2.9444 | -15.8889 | 0 | 0 | 0 | 0 | 0 | 0 |  | 199 | 284 | 450 | I | 3.6957 | -67.087 | 0 | 0 | 0 | 0 | 0 | 0
[21 empty] | 400 | 180 | 330 | 300 | I | 1 | 3.333 | -120 | 0 | 0 | 0 | 0 | 0 | 0 |  | 255 | 330 | 500 | I | 3 | -21 | 0 | 0 | 0 | 0 | 0 | 0 |  | 284 | 330 | 450 | I | 4.6 | -153 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 133 | 175 | 350 | I | 1 | 2.8 | -49 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 50 | J | 1.0732 | -3.0244 | 0 | 0 | 0 | 0 | 0 | 0 |  | 115 | 202 | 500 | I | 2.2174 | 73.3913 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 175 | 235 | 350 | I | 1 | 3 | -65 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 201 | 50 | J | 2.1042 | -102 | 0 | 0 | 0 | 0 | 0 | 0 |  | 202 | 255 | 500 | I | 2.9444 | 31.2222 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 235 | 330 | 350 | I | 1 | 3.519 | -116.85 | 0 | 0 | 0 | 0 | 0 | 0 |  | 201 | 300 | 50 | J | 3.7198 | -334.6443 | 0 | 0 | 0 | 0 | 0 | 0 |  | 255 | 330 | 500 | I | 3.9474 | -45 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 158 | 200 | 400 | I | 1 | 3 | -37 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 99 | 100 | J | 1.1 | -2.2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 50 | J | 1.0417 | -2.6042 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 200 | 235 | 400 | I | 1 | 3.181 | -51.363 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99 | 206 | 100 | J | 2.14 | -97.88 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 50 | J | 2.2472 | -121.3483 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 235 | 265 | 400 | I | 1 | 3 | -35 | 0 | 0 | 0 | 0 | 0 | 0 |  | 206 | 300 | 100 | J | 3.3904 | -275.4342 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 50 | J | 3.4483 | -293.1034 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 265 | 330 | 400 | I | 1 | 3.421 | -77.105 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 99 | 150 | J | 1.1316 | 0.55263 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 100 | J | 1.2195 | -7.3171 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 163 | 220 | 450 | I | 1 | 2.85 | -22.25 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99 | 203 | 150 | J | 2.1224 | -85.6531 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 200 | 100 | J | 2.1978 | -93.4066 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 220 | 254 | 450 | I | 1 | 3.4 | -69 | 0 | 0 | 0 | 0 | 0 | 0 |  | 203 | 300 | 150 | J | 3.4729 | -269.3119 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 300 | 100 | J | 2.8986 | -186.9565 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 254 | 268 | 450 | I | 1 | 2.8 | -12 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 99 | 200 | J | 1.2703 | -3.8919 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 150 | J | 1.25 | -1.875 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 268 | 330 | 450 | I | 1 | 4.429 | -174.86 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99 | 201 | 200 | J | 2.125 | -73.125 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 150 | 150 | J | 2.0408 | -66.3265 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 180 | 215 | 500 | I | 1 | 3.5 | -47.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 201 | 300 | 200 | J | 3.1935 | -210.9677 | 0 | 0 | 0 | 0 | 0 | 0 |  | 150 | 300 | 150 | J | 2.5641 | -121.7949 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 215 | 255 | 500 | I | 1 | 4 | -85 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 95 | 250 | J | 1.2857 | 1.1429 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 200 | J | 1.3333 | -0.66667 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 255 | 280 | 500 | I | 1 | 5 | -170 | 0 | 0 | 0 | 0 | 0 | 0 |  | 95 | 200 | 250 | J | 2.1429 | -61.4286 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 150 | 200 | J | 2.2222 | -67.7778 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 280 | 330 | 500 | I | 1 | 5.555 | -220 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 200 | 300 | 250 | J | 3.1835 | -188.3895 | 0 | 0 | 0 | 0 | 0 | 0 |  | 150 | 300 | 200 | J | 2.5641 | -101.2821 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 70 | 50 | J | 1-1/16 | 1.111 | -2.222 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 105 | 300 | J | 1.4359 | 1.6154 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 250 | J | 1.3333 | 11.3333 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 70 | 100 | 50 | J | 1-1/16 | 1.111 | -2.222 | 0 | 0 | 0 | 0 | 0 | 0 |  | 105 | 194 | 300 | J | 2.225 | -55.2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 150 | 250 | J | 1.9608 | -30.3922 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 100 | 114 | 50 | J | 1-1/16 | 1.75 | -61 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 194 | 300 | 300 | J | 3.0319 | -145.5768 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 150 | 300 | 250 | J | 2.8571 | -112.8571 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 114 | 165 | 50 | J | 1-1/16 | 2.55 | -141 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 101 | 350 | J | 1.4571 | 12.1143 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 300 | J | 1.3699 | 20.5479 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 164 | 188 | 50 | J | 1-1/16 | 2.4 | -124 | 0 | 0 | 0 | 0 | 0 | 0 |  | 101 | 206 | 350 | J | 2.2826 | -38.2391 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 150 | 300 | J | 2 | -16 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 188 | 300 | 50 | J | 1-1/16 | 2.723 | -165.99 | 0 | 0 | 0 | 0 | 0 | 0 |  | 206 | 300 | 350 | J | 2.9688 | -111.6562 | 0 | 0 | 0 | 0 | 0 | 0 | 400 | 150 | 300 | 300 | J | 2.6316 | -68.4211 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 74 | 100 | J | 1-1/16 | 1.2 | -4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 96 | 400 | J | 1.5161 | 17.1613 | 0 | 0 | 0 | 0 | 0 | 0 |  | 55 | 100 | 350 | J | 1.4085 | 31.6901 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 74 | 100 | 100 | J | 1-1/16 | 1.238 | -6.476 | 0 | 0 | 0 | 0 | 0 | 0 |  | 96 | 202 | 400 | J | 2.3556 | -26.4889 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 150 | 350 | J | 1.9608 | 4.902 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 100 | 120 | 100 | J | 1-1/16 | 2 | -72 | 0 | 0 | 0 | 0 | 0 | 0 |  | 202 | 300 | 400 | J | 2.9032 | -79.6129 | 0 | 0 | 0 | 0 | 0 | 0 |  | 150 | 300 | 350 | J | 2.5 | -35 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 120 | 177 | 100 | J | 1-1/16 | 2.375 | -108 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 112 | 450 | J | 1.7273 | 20.4545 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99 | 150 | 400 | J | 1.6949 | 39.8305 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 177 | 300 | 100 | J | 1-1/16 | 2.674 | -143.87 | 0 | 0 | 0 | 0 | 0 | 0 |  | 112 | 199 | 450 | J | 2.4857 | -19.7429 | 0 | 0 | 0 | 0 | 0 | 0 |  | 150 | 300 | 400 | J | 2.0833 | 14.5833 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 80 | 150 | J | 1-1/16 | 1.2 | 2 | 0 | 0 | 0 | 0 | 0 | 0 |  | 199 | 300 | 450 | J | 2.7667 | -44.4667 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 150 | 450 | J | 1.5385 | 70 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 80 | 100 | 150 | J | 1-1/16 | 1.333 | -6.666 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99 | 199 | 500 | J | 2.5278 | -5.75 | 0 | 0 | 0 | 0 | 0 | 0 |  | 150 | 300 | 450 | J | 1.8868 | 51.8868 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 100 | 118 | 150 | J | 1-1/16 | 1.8 | -44 | 0 | 0 | 0 | 0 | 0 | 0 |  | 199 | 300 | 500 | J | 3 | -44 | 0 | 0 | 0 | 0 | 0 | 0 |  | 110 | 150 | 500 | J | 1.8868 | 74.5283 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 118 | 142 | 150 | J | 1-1/16 | 2.4 | -98 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 101 | 50 | K | 1.0417 | -0.041667 | 0 | 0 | 0 | 0 | 0 | 0 |  | 150 | 300 | 500 | J | 2 | 70 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 142 | 300 | 150 | J | 1-1/16 | 2.59 | -117.02 | 0 | 0 | 0 | 0 | 0 | 0 |  | 101 | 150 | 50 | K | 1.4412 | -38.7941 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 99 | 50 | K | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 86 | 200 | J | 1-1/16 | 1.286 | 2.429 | 0 | 0 | 0 | 0 | 0 | 0 |  | 150 | 200 | 50 | K | 2.5 | -177.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99 | 150 | 50 | K | 1.7586 | -75.1034 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 86 | 100 | 200 | J | 1-1/16 | 1.4 | -5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 262 | 50 | K | 3.3428 | -304.767 | 0 | 0 | 0 | 0 | 0 | 0 |  | 150 | 200 | 50 | K | 2.381 | -154.7619 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 100 | 110 | 200 | J | 1-1/16 | 2 | -50 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 100 | K | 1.0889 | -1.2667 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 262 | 50 | K | 3.4444 | -313.2222 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 110 | 160 | 200 | J | 1-1/16 | 2.5 | -90 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 150 | 100 | K | 1.4706 | -36.7647 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 99 | 100 | K | 1.2 | -7.8 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 160 | 300 | 200 | J | 1-1/16 | 2.979 | -137.87 | 0 | 0 | 0 | 0 | 0 | 0 |  | 150 | 198 | 100 | K | 2.4 | -154.8 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99 | 150 | 100 | K | 1.7 | -52.3 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 92 | 250 | J | 1-1/16 | 1.235 | 11.706 | 0 | 0 | 0 | 0 | 0 | 0 |  | 198 | 262 | 100 | K | 3.5 | -316.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 150 | 199 | 100 | K | 2.45 | -141.55 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 92 | 120 | 250 | J | 1-1/16 | 1.866 | -29.333 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 150 | K | 1.0889 | 3.0889 | 0 | 0 | 0 | 0 | 0 | 0 |  | 199 | 262 | 100 | K | 2.7391 | -181.7391 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 120 | 174 | 250 | J | 1-1/16 | 2.7 | -96 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 152 | 150 | K | 1.5758 | -40.2424 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 98 | 150 | K | 1.225 | -3.675 | 0 | 0 | 0 | 0 | 0 | 0
[21 empty] | 400 | 174 | 300 | 250 | J | 1-1/16 | 3.15 | -141 | 0 | 0 | 0 | 0 | 0 | 0 |  | 152 | 198 | 150 | K | 2.5556 | -159.7778 | 0 | 0 | 0 | 0 | 0 | 0 |  | 98 | 149 | 150 | K | 1.7586 | -47.9655 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 100 | 300 | J | 1-1/16 | 1.25 | 18.75 | 0 | 0 | 0 | 0 | 0 | 0 |  | 198 | 262 | 150 | K | 3.2 | -250 | 0 | 0 | 0 | 0 | 0 | 0 |  | 149 | 198 | 150 | K | 2.5789 | -139.8421 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 100 | 120 | 300 | J | 1-1/16 | 2 | -30 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 102 | 200 | K | 1.1778 | 0.71111 | 0 | 0 | 0 | 0 | 0 | 0 |  | 198 | 262 | 150 | K | 2.9091 | -183.0909 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 120 | 162 | 300 | J | 1-1/16 | 3 | -105 | 0 | 0 | 0 | 0 | 0 | 0 |  | 102 | 150 | 200 | K | 1.6552 | -40.3448 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 200 | K | 1.2195 | 3.6585 | 0 | 0 | 0 | 0 | 0 | 0
[21 empty] | 400 | 162 | 300 | 300 | J | 1-1/16 | 3.136 | -117.14 | 0 | 0 | 0 | 0 | 0 | 0 |  | 150 | 201 | 200 | K | 2.55 | -143.25 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 151 | 200 | K | 1.8889 | -49.2222 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 115 | 153 | 350 | J | 1-1/16 | 2.533 | -49.666 | 0 | 0 | 0 | 0 | 0 | 0 |  | 201 | 262 | 200 | K | 3.125 | -220.875 | 0 | 0 | 0 | 0 | 0 | 0 |  | 151 | 201 | 200 | K | 2.6316 | -127.9474 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 153 | 209 | 350 | J | 1-1/16 | 2.8 | -71 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 99 | 250 | K | 1.2821 | -1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 201 | 262 | 200 | K | 2.9048 | -162.0952 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 209 | 300 | 350 | J | 1-1/16 | 3.138 | -104.79 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99 | 149 | 250 | K | 1.6667 | -31 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 98 | 250 | K | 1.2895 | 9.0263 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 132 | 147 | 400 | J | 1-1/16 | 3 | -63 | 0 | 0 | 0 | 0 | 0 | 0 |  | 149 | 200 | 250 | K | 2.55 | -126.4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 98 | 149 | 250 | K | 1.7586 | -23.3448 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 147 | 233 | 400 | J | 1-1/16 | 2.866 | -53.666 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 200 | 262 | 250 | K | 3.0625 | -192 | 0 | 0 | 0 | 0 | 0 | 0 |  | 149 | 200 | 250 | K | 2.6842 | -114.0526 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 233 | 300 | 400 | J | 1-1/16 | 3.19 | -86.048 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 95 | 300 | K | 1.2571 | 8.2571 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 200 | 262 | 250 | K | 3.2632 | -181.7895 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 150 | 160 | 450 | J | 1-1/16 | 2 | 20 | 0 | 0 | 0 | 0 | 0 | 0 |  | 95 | 152 | 300 | K | 1.8387 | -31.871 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 98 | 300 | K | 1.2 | 23.6 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 160 | 174 | 450 | J | 1-1/16 | 2.8 | -36 | 0 | 0 | 0 | 0 | 0 | 0 |  | 152 | 196 | 300 | K | 2.4444 | -92.4444 | 0 | 0 | 0 | 0 | 0 | 0 |  | 98 | 148 | 300 | K | 1.7241 | -8.8966 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 174 | 197 | 450 | J | 1-1/16 | 2.555 | -17.666 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 196 | 262 | 300 | K | 2.8696 | -142.6087 | 0 | 0 | 0 | 0 | 0 | 0 |  | 148 | 201 | 300 | K | 2.7895 | -105.8421 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 197 | 300 | 450 | J | 1-1/16 | 2.5122 | -14.024 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 93 | 350 | K | 1.3793 | 10.2414 | 0 | 0 | 0 | 0 | 0 | 0 | 349 | 201 | 262 | 300 | K | 3.5882 | -193.7059 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 164 | 180 | 500 | J | 1-1/16 | 3.2 | -44 | 0 | 0 | 0 | 0 | 0 | 0 |  | 93 | 147 | 350 | K | 1.8 | -15 | 0 | 0 | 0 | 0 | 0 | 0 |  | 60 | 99 | 350 | K | 1.1714 | 40.4286 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 180 | 194 | 500 | J | 1-1/16 | 2.8 | -16 | 0 | 0 | 0 | 0 | 0 | 0 |  | 147 | 200 | 350 | K | 2.5238 | -80.1429 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99 | 150 | 350 | K | 1.7 | 14 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 194 | 230 | 500 | J | 1-1/16 | 3.6 | -76 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 262 | 350 | K | 2.813 | -112.2389 | 0 | 0 | 0 | 0 | 0 | 0 |  | 150 | 200 | 350 | K | 2.381 | -40.4762 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 230 | 250 | 500 | J | 1-1/16 | 4 | -110 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 109 | 400 | K | 1.5 | 13 | 0 | 0 | 0 | 0 | 0 | 0 |  | 200 | 262 | 350 | K | 3.3333 | -136.6667 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 250 | 300 | 500 | J | 1-1/16 | 4.545 | -159.09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 109 | 155 | 400 | K | 2.1905 | -31.1905 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99 | 150 | 400 | K | 1.5484 | 40.0645 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 70 | 50 | K | 1-1/8 | 1.176 | -6.471 | 0 | 0 | 0 | 0 | 0 | 0 |  | 155 | 201 | 400 | K | 2.7059 | -75 | 0 | 0 | 0 | 0 | 0 | 0 |  | 150 | 203 | 400 | K | 2.3043 | -13.6087 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 70 | 107 | 50 | K | 1-1/8 | 1.057 | 1.286 | 0 | 0 | 0 | 0 | 0 | 0 |  | 201 | 262 | 400 | K | 2.6842 | -72.7895 | 0 | 0 | 0 | 0 | 0 | 0 |  | 203 | 262 | 400 | K | 3.2778 | -105.1111 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 107 | 145 | 50 | K | 1-1/8 | 1.9 | -83 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 106 | 450 | K | 1.6061 | 19.2727 | 0 | 0 | 0 | 0 | 0 | 0 |  | 95 | 148 | 450 | K | 1.3243 | 71.1892 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 145 | 168 | 50 | K | 1-1/8 | 2.3 | -131 | 0 | 0 | 0 | 0 | 0 | 0 |  | 106 | 152 | 450 | K | 2.0909 | -6.9091 | 0 | 0 | 0 | 0 | 0 | 0 |  | 148 | 199 | 450 | K | 1.8889 | 38.4444 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 168 | 197 | 50 | K | 1-1/8 | 2.9 | -209 | 0 | 0 | 0 | 0 | 0 | 0 |  | 152 | 196 | 450 | K | 2.5882 | -44.7059 | 0 | 0 | 0 | 0 | 0 | 0 |  | 199 | 262 | 450 | K | 3.7059 | -116 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 197 | 262 | 50 | K | 1-1/8 | 2.26 | -119.4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 196 | 262 | 450 | K | 2.9126 | -74.8693 | 0 | 0 | 0 | 0 | 0 | 0 |  | 105 | 149 | 500 | K | 1.6333 | 75.5 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 72 | 100 | K | 1-1/8 | 1.1 | 0.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99 | 148 | 500 | K | 2.1364 | 2.7273 | 0 | 0 | 0 | 0 | 0 | 0 |  | 149 | 202 | 500 | K | 1.8929 | 63.8214 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 72 | 95 | 100 | K | 1-1/8 | 1.095 | 0.806 | 0 | 0 | 0 | 0 | 0 | 0 |  | 148 | 201 | 500 | K | 2.7895 | -41.6842 | 0 | 0 | 0 | 0 | 0 | 0 |  | 202 | 262 | 500 | K | 3 | -17 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 95 | 112 | 100 | K | 1-1/8 | 1.545 | -37.909 | 0 | 0 | 0 | 0 | 0 | 0 |  | 201 | 262 | 500 | K | 2.7886 | -41.6057 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 50 | L | 0.9901 | 0.49505 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 112 | 158 | 100 | K | 1-1/8 | 2 | -82 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 50 | L | 1.02 | -0.98 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 150 | 50 | L | 1.4493 | -45.6522 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 158 | 180 | 100 | K | 1-1/8 | 2.2 | -106 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 145 | 50 | L | 1.2857 | -27.2857 | 0 | 0 | 0 | 0 | 0 | 0 |  | 150 | 200 | 50 | L | 2.381 | -171.4286 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 180 | 262 | 100 | K | 1-1/8 | 2.485 | -143.03 | 0 | 0 | 0 | 0 | 0 | 0 |  | 145 | 200 | 50 | L | 2.3913 | -175.4348 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 100 | L | 1.0753 | -3.7634 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 76 | 150 | K | 1-1/8 | 1.04 | 8.4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 100 | L | 1.0851 | -4.1702 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 150 | 100 | L | 1.6949 | -63.5593 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 76 | 93 | 150 | K | 1-1/8 | 1.133 | 2.333 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 149 | 100 | L | 1.2895 | -23.7895 | 0 | 0 | 0 | 0 | 0 | 0 |  | 150 | 200 | 100 | L | 2.5 | -165 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 93 | 107 | 150 | K | 1-1/8 | 1.4 | -19 | 0 | 0 | 0 | 0 | 0 | 0 |  | 149 | 200 | 100 | L | 2.55 | -192.7 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 150 | L | 1.0989 | 0.54945 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 107 | 128 | 150 | K | 1-1/8 | 2.1 | -82 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 150 | L | 1.087 | -1.087 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 150 | 150 | L | 1.8868 | -70.7547 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 128 | 262 | 150 | K | 1-1/8 | 2.351 | -107.09 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 148 | 150 | L | 1.4545 | -35.2727 | 0 | 0 | 0 | 0 | 0 | 0 |  | 150 | 200 | 150 | L | 2.5 | -142.5 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 80 | 200 | K | 1-1/8 | 1.071 | 10.357 | 0 | 0 | 0 | 0 | 0 | 0 |  | 148 | 200 | 150 | L | 2.6 | -179.6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 200 | L | 1.0417 | 9.375 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 80 | 100 | 200 | K | 1-1/8 | 1.333 | -6.666 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 200 | L | 1.1304 | 0.52174 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 150 | 200 | L | 2.0833 | -81.25 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 100 | 120 | 200 | K | 1-1/8 | 2 | -60 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 149 | 200 | L | 1.4848 | -30.6667 | 0 | 0 | 0 | 0 | 0 | 0 |  | 150 | 200 | 200 | L | 2.7778 | -158.3333 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 120 | 173 | 200 | K | 1-1/8 | 2.65 | -118.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 149 | 200 | 200 | L | 2.6842 | -175.7895 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 250 | L | 1.0753 | 15.5914 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 173 | 262 | 200 | K | 1-1/8 | 2.967 | -153.33 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 250 | L | 1.2439 | -3.2439 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 150 | 250 | L | 1.8868 | -48.1132 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 88 | 250 | K | 1-18 | 1.118 | 15.3529 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 149 | 250 | L | 1.4848 | -23.2424 | 0 | 0 | 0 | 0 | 0 | 0 | 252 | 150 | 200 | 250 | L | 2.7027 | -133.7838 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 88 | 110 | 250 | K | 1-18 | 1.466 | -7.333 | 0 | 0 | 0 | 0 | 0 | 0 | 252 | 149 | 200 | 250 | L | 2.6842 | -162.3684 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 300 | L | 1.0989 | 23.6264 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 110 | 120 | 250 | K | 1-18 | 2 | -50 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 300 | L | 1.3333 | -2.6667 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 150 | 300 | L | 1.8868 | -31.1321 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 120 | 160 | 250 | K | 1-18 | 2.5 | -92.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 147 | 300 | L | 1.6786 | -29.25 | 0 | 0 | 0 | 0 | 0 | 0 | 252 | 150 | 200 | 300 | L | 2.6316 | -102.6316 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 160 | 200 | 250 | K | 1-18 | 2.857 | -128.571 | 0 | 0 | 0 | 0 | 0 | 0 | 252 | 147 | 200 | 300 | L | 2.4091 | -105.9545 | 0 | 0 | 0 | 0 | 0 | 0 |  | 50 | 100 | 350 | L | 1.1494 | 31.6092 | 0 | 0 | 0 | 0 | 0 | 0
[21 empty] | 349 | 200 | 262 | 250 | K | 1-18 | 3.1 | -156.5 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 350 | L | 1.3158 | 5.2632 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 150 | 350 | L | 1.9608 | -16.6667 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 90 | 300 | K | 1-1/8 | 1 | 25 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 148 | 350 | L | 1.7778 | -28 | 0 | 0 | 0 | 0 | 0 | 0 |  | 150 | 200 | 350 | L | 2.3256 | -47.6744 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 90 | 118 | 300 | K | 1-1/8 | 1.866 | -31.333 | 0 | 0 | 0 | 0 | 0 | 0 |  | 148 | 200 | 350 | L | 2.6 | -109.4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 60 | 100 | 400 | L | 1.2821 | 34.6154 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 118 | 170 | 300 | K | 1-1/8 | 2.6 | -90 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 400 | L | 1.3889 | 9.7222 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 150 | 400 | L | 1.7241 | 12.069 | 0 | 0 | 0 | 0 | 0 | 0
[21 empty] | 349 | 170 | 262 | 300 | K | 1-1/8 | 3.286 | -158.57 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 148 | 400 | L | 1.92 | -24.8 | 0 | 0 | 0 | 0 | 0 | 0 |  | 150 | 200 | 400 | L | 2.2727 | -31.8182 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 92 | 100 | 350 | K | 1-1/8 | 1.6 | -4 | 0 | 0 | 0 | 0 | 0 | 0 |  | 148 | 200 | 400 | L | 2.4762 | -74.8571 | 0 | 0 | 0 | 0 | 0 | 0 |  | 90 | 150 | 450 | L | 1.1628 | 68.6047 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 100 | 183 | 350 | K | 1-1/8 | 2.371 | -54.143 | 0 | 0 | 0 | 0 | 0 | 0 |  | 49 | 100 | 450 | L | 1.4722 | 16.0833 | 0 | 0 | 0 | 0 | 0 | 0 |  | 150 | 200 | 450 | L | 2.0833 | 4.1667 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 183 | 262 | 350 | K | 1-1/8 | 2.633 | -80.333 | 0 | 0 | 0 | 0 | 0 | 0 |  | 100 | 148 | 450 | L | 1.92 | -9.44 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99 | 150 | 500 | L | 1.2821 | 74.359 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 112 | 150 | 400 | K | 1-1/8 | 2.533 | -52.666 | 0 | 0 | 0 | 0 | 0 | 0 |  | 148 | 200 | 450 | L | 2.5238 | -58.9524 | 0 | 0 | 0 | 0 | 0 | 0 |  | 150 | 200 | 500 | L | 1.9231 | 36.5385 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 150 | 200 | 400 | K | 1-1/8 | 2.5 | -50 | 0 | 0 | 0 | 0 | 0 | 0 |  | 99 | 152 | 500 | L | 1.9259 | 3.7037 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 200 | 262 | 400 | K | 1-1/8 | 2.952 | -95.238 | 0 | 0 | 0 | 0 | 0 | 0 |  | 152 | 200 | 500 | L | 2.7778 | -61.8889 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 140 | 158 | 450 | K | 1-1/8 | 1.8 | 23 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 158 | 170 | 450 | K | 1-1/8 | 2.4 | -22 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 170 | 178 | 450 | K | 1-1/8 | 1.6 | 42 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 178 | 262 | 450 | K | 1-1/8 | 2.27 | -14.973 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 146 | 155 | 500 | K | 1-1/8 | 1.8 | 29 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 155 | 184 | 500 | K | 1-1/8 | 2.9 | -48 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 184 | 215 | 500 | K | 1-1/8 | 3.1 | -64 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 215 | 262 | 500 | K | 1-1/8 | 3.917 | -137.5 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 66 | 50 | L | 1-3/16 | 0.941 | 4.823 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 66 | 99 | 50 | L | 1-3/16 | 0.943 | 4.714 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 99 | 112 | 50 | L | 1-3/16 | 1.3 | -31 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 112 | 153 | 50 | L | 1-3/16 | 2.05 | -113.5 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 153 | 200 | 50 | L | 1-3/16 | 2.35 | -152.5 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 70 | 100 | L | 1-3/16 | 1 | 5 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 70 | 93 | 100 | L | 1-3/16 | 0.92 | 10.2 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 93 | 105 | 100 | L | 1-3/16 | 1.2 | -15 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 105 | 145 | 100 | L | 1-3/16 | 2 | -95 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 145 | 200 | 100 | L | 1-3/16 | 2.25 | -125.02 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 73 | 150 | L | 1-3/16 | 0.92 | 13.2 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 73 | 89 | 150 | L | 1-3/16 | 1.066 | 3.666 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 89 | 100 | 150 | L | 1-3/16 | 1.1 | 1 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 100 | 107 | 150 | L | 1-3/16 | 1.75 | -57.5 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 107 | 140 | 150 | L | 1-3/16 | 2.063 | -86.875 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 140 | 161 | 150 | L | 1-3/16 | 2.1 | -91 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 161 | 200 | 150 | L | 1-3/16 | 2.294 | -114.3 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 78 | 200 | L | 1-3/16 | 1 | 13 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 78 | 93 | 200 | L | 1-3/16 | 1 | 13 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 93 | 110 | 200 | L | 1-3/16 | 1.7 | -43 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 110 | 160 | 200 | L | 1-3/16 | 2.5 | -115 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 160 | 200 | 200 | L | 1-3/16 | 3.077 | -178.46 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 85 | 250 | L | 1-1/16 | 1.029 | 18.089 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 85 | 100 | 250 | L | 1-1/16 | 1 | 20 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 100 | 120 | 250 | L | 1-1/16 | 2 | -60 | 0 | 0 | 0 | 0 | 0 | 0
[21 empty] | 252 | 120 | 200 | 250 | L | 1-1/16 | 2.5 | -105 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 50 | 90 | 300 | L | 1-3/16 | 1.026 | 23.333 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 90 | 100 | 300 | L | 1-3/16 | 1 | 25 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 100 | 120 | 300 | L | 1-3/16 | 2 | -50 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 120 | 160 | 300 | L | 1-3/16 | 2.666 | -106.666 | 0 | 0 | 0 | 0 | 0 | 0
[21 empty] | 252 | 160 | 200 | 300 | L | 1-3/16 | 3.077 | -147.69 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 87 | 95 | 350 | L | 1-3/16 | 1.6 | -9 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 95 | 127 | 350 | L | 1-3/16 | 2.133 | -43.666 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 127 | 150 | 350 | L | 1-3/16 | 2.3 | -57 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 150 | 172 | 350 | L | 1-3/16 | 2.2 | -48 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 172 | 200 | 350 | L | 1-3/16 | 2.333 | -61.333 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 96 | 105 | 400 | L | 1-3/16 | 1.8 | -12 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 105 | 120 | 400 | L | 1-3/16 | 2.5 | -57.5 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 120 | 140 | 400 | L | 1-3/16 | 2.222 | -37.777 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 140 | 200 | 400 | L | 1-3/16 | 2.5 | -60 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 130 | 148 | 450 | L | 1-3/16 | 1.8 | 13 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 148 | 160 | 450 | L | 1-3/16 | 2.4 | -32 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 160 | 177 | 450 | L | 1-3/16 | 1.7 | 24 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 177 | 200 | 450 | L | 1-3/16 | 2.3 | -30 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 135 | 145 | 500 | L | 1-3/16 | 2 | 5 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 145 | 180 | 500 | L | 1-3/16 | 2.333 | -18.333 | 0 | 0 | 0 | 0 | 0 | 0
[22 empty] | 180 | 200 | 500 | L | 1-3/16 | 2.857 | -62.87 | 0 | 0 | 0 | 0 | 0 | 0

## Z2100 Series
[6 empty] | Qty | Floor | Stair / Standpipe | Static Inlet (psi) | Residual Inlet (psi) | Flow (gpm) | Desired Residual Outlet Min (psi) | Desired Residual Outlet Max (psi) | Valve Setting | Actual Static Outlet | Actual Residual Outlet | Model (Part Number)
|  | Fire Valve sizing, Adjustable | [15 empty] | 429 | 2 | 25 | 70 | 100 | 400 | 0 | A | 3/16 | 6.666 | -66.666 | 0 | 0
For all 1-1/2" Z2100 series valves (DISCONTINUED) | [17 empty] | 430 | 2 | 32 | 77 | 100 | 400 | 0 | B | 1/4 | 6.666 | -113.333 | 0 | 0
Step 1: Enter the static, residual, and flow data in the three green boxes (required) (See tabs below for other models) | [17 empty] | 431 | 2 | 39 | 84 | 100 | 400 | 0 | C | 5/16 | 6.666 | -160 | 0 | 0
Step 2: Enter desired residual outlet pressure to identify closest setting (optional) | [17 empty] | 432 | 2 | 47 | 91 | 100 | 400 | 0 | D | 3/8 | 6.818 | -220.454 | 0 | 0
Step 3: Outlet pressure values will appear below for each setting choice, then select model and closest setting | [17 empty] | 433 | 2 | 49 | 54 | 100 | 120 | 0 | E | 7/16 | 4 | -96 | 0 | 0
|  |  |  | Desired | [13 empty] | 434 | 2 | 54 | 60 | 120 | 150 | 0 | E | 7/16 | 5 | -150 | 0 | 0
| Static | Residual | Flow | Residual | [13 empty] | 435 | 2 | 60 | 98 | 150 | 400 | 0 | E | 7/16 | 6.579 | -244.74 | 0 | 0
| Inlet (psi) | Inlet (psi) | (gpm) | Outlet | [13 empty] | 436 | 2 | 49 | 60 | 100 | 125 | 0 | F | 1/2 | 2.272 | -11.363 | 0 | 0
[18 empty] | 437 | 2 | 60 | 67 | 125 | 150 | 0 | F | 1/2 | 3.571 | -89.286 | 0 | 0
[18 empty] | 438 | 2 | 67 | 106 | 150 | 400 | 0 | F | 1/2 | 6.41 | -279.49 | 0 | 0
| Models: Z2100, Z2105 | [16 empty] | 439 | 2 | 49 | 66 | 100 | 120 | 0 | G | 9/16 | 1.176 | 42.353 | 0 | 0
| Angle Body | Static | Residual | Difference | Floor Worksheet Instructions | [12 empty] | 440 | 2 | 66 | 75 | 120 | 150 | 0 | G | 9/16 | 3.333 | -100 | 0 | 0
| Setting | Outlet | Outlet | to desired | 1. Copy green input values and paste to Columns J, K, L | [12 empty] | 441 | 2 | 75 | 114 | 150 | 400 | 0 | G | 9/16 | 6.41 | -330.77 | 0 | 0
| A | 0 | 0 | 0 | for each floor | [14 empty] | 22 | 31 | 50 | 100 | 25 | A |  | 5.5556 | -72.2222 | 0 | 0 | 0 | 0 | 0 | 0
| B | 0 | 0 | 0 | 2. Copy selected Bonnet Type, Static Outlet | [14 empty] | 31 | 39 | 100 | 160 | 25 | A |  | 7.5 | -132.5 | 0 | 0 | 0 | 0 | 0 | 0
| C | 0 | 0 | 0 | and Residual Outlet values | [14 empty] | 39 | 52 | 160 | 260 | 25 | A |  | 7.6923 | -140 | 0 | 0 | 0 | 0 | 0 | 0
| D | 0 | 0 | 0 | 3. Paste values to Valve Setting, Actual Static Outlet, | [14 empty] | 52 | 60.5 | 260 | 350 | 25 | A |  | 10.5882 | -290.5882 | 0 | 0 | 0 | 0 | 0 | 0
| E | 0 | 0 | 0 | and Actual Residual Outlet columns P, Q, R | [14 empty] | 60.5 | 64 | 350 | 400 | 25 | A |  | 14.2857 | -514.2857 | 0 | 0 | 0 | 0 | 0 | 0
| F | 0 | 0 | 0 | 4. Copy and paste Part Number created from | [12 empty] | 442 | 2 | 11 | 24 | 50 | 120 | 50 | A | 3/16 | 5.385 | -9.231 | 0 | 0 | 0 | 0 | 0 | 0
| G | 0 | 0 | 0 | Part Number Assistant tab to column S | [12 empty] | 443 | 2 | 24 | 31 | 120 | 160 | 50 | A | 3/16 | 5.714 | -17.143 | 0 | 0 | 0 | 0 | 0 | 0
NOTES: |  |  |  |  | 5. Input remaining data to columns G, H, I, M, N | [12 empty] | 444 | 2 | 31 | 52 | 160 | 320 | 50 | A | 3/16 | 7.619 | -76.19 | 0 | 0 | 0 | 0 | 0 | 0
All calculated outlet pressures have a tolerance +/- 10% | [17 empty] | 445 | 2 | 52 | 59 | 320 | 400 | 50 | A | 3/16 | 11.429 | -274.286 | 0 | 0 | 0 | 0 | 0 | 0
Static and Residual Outlet values must be below 175 PSI for UL approval (Values exceeding 175 PSI will be highlighted RED) | [17 empty] | 501 | 2 | 10 | 20 | 91 | 140 | 75 | A | 3/16 | 4.9 | 42 | 0 | 0 | 0 | 0 | 0 | 0
Refer to Part Number Assistant tab below to get help with part numbers | [17 empty] | 502 | 2 | 20 | 30 | 140 | 210 | 75 | A | 3/16 | 7 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 503 | 2 | 30 | 41 | 210 | 300 | 75 | A | 3/16 | 8.181 | -35.454 | 0 | 0 | 0 | 0 | 0 | 0
Zurn Water, LLC ¦ Wilkins | [17 empty] | 504 | 2 | 41 | 51 | 300 | 400 | 75 | A | 3/16 | 10 | -110 | 0 | 0 | 0 | 0 | 0 | 0
1747 Commerce Way, Paso Robles, CA 93446 USA | [17 empty] | 470 | 2 | 10 | 20 | 114 | 178 | 100 | A | 3/16 | 6.4 | 50 | 0 | 0 | 0 | 0 | 0 | 0
Ph. 855-663-9876 | [17 empty] | 471 | 2 | 20 | 30 | 178 | 266 | 100 | A | 3/16 | 8.8 | 2 | 0 | 0 | 0 | 0 | 0 | 0
ZURN.COM | [17 empty] | 472 | 2 | 30 | 41 | 266 | 400 | 100 | A | 3/16 | 12.181 | -99.454 | 0 | 0 | 0 | 0 | 0 | 0
REV 4/8/2024 | [17 empty] | 536 | 2 | 10 | 20 | 184 | 233 | 125 | A | 3/16 | 4.9 | 135 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 537 | 2 | 20 | 30 | 233 | 300 | 125 | A | 3/16 | 6.7 | 99 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 538 | 2 | 30 | 40 | 300 | 400 | 125 | A | 3/16 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 29 | 42 | 50 | 120 | 25 | B |  | 5.3846 | -106.1538 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 42 | 53 | 120 | 200 | 25 | B |  | 7.2727 | -185.4545 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 53 | 62 | 200 | 280 | 25 | B |  | 8.8889 | -271.1111 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 62 | 72.5 | 280 | 400 | 25 | B |  | 11.4286 | -428.5714 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 446 | 2 | 17 | 32 | 50 | 120 | 50 | B | 1/4 | 4.666 | -29.333 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 447 | 2 | 32 | 53 | 120 | 260 | 50 | B | 1/4 | 6.666 | -93.333 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 448 | 2 | 53 | 62 | 260 | 340 | 50 | B | 1/4 | 8.888 | -211.111 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 449 | 2 | 62 | 68 | 340 | 400 | 50 | B | 1/4 | 10 | -280 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 505 | 2 | 10 | 30 | 70 | 150 | 75 | B | 1/4 | 4 | 30 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 506 | 2 | 30 | 40 | 150 | 215 | 75 | B | 1/4 | 6.5 | -45 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 507 | 2 | 40 | 50 | 215 | 300 | 75 | B | 1/4 | 8.5 | -125 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 508 | 2 | 50 | 59 | 300 | 400 | 75 | B | 1/4 | 11.111 | -255.555 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 473 | 2 | 10 | 20 | 97 | 139 | 100 | B | 1/4 | 4.2 | 55 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 474 | 2 | 20 | 30 | 139 | 206 | 100 | B | 1/4 | 6.7 | 5 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 475 | 2 | 30 | 41 | 206 | 300 | 100 | B | 1/4 | 8.545 | -50.363 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 476 | 2 | 41 | 49 | 300 | 400 | 100 | B | 1/4 | 12.5 | -212.5 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 539 | 2 | 10 | 20 | 155 | 195 | 125 | B | 1/4 | 4 | 115 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 540 | 2 | 20 | 30 | 195 | 255 | 125 | B | 1/4 | 6 | 75 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 541 | 2 | 30 | 40 | 255 | 340 | 125 | B | 1/4 | 8.5 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 542 | 2 | 40 | 44 | 340 | 400 | 125 | B | 1/4 | 15 | -260 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 32 | 44 | 50 | 100 | 25 | C |  | 4.1667 | -83.3333 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 44 | 51 | 100 | 140 | 25 | C |  | 5.7143 | -151.4286 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 51 | 62 | 140 | 220 | 25 | C |  | 7.2727 | -230.9091 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 62 | 72 | 220 | 300 | 25 | C |  | 8 | -276 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 72 | 82 | 300 | 400 | 25 | C |  | 10 | -420 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 450 | 2 | 21 | 40 | 50 | 130 | 50 | C | 5/16 | 4.211 | -38.421 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 451 | 2 | 40 | 62 | 130 | 280 | 50 | C | 5/16 | 6.818 | -142.727 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 452 | 2 | 62 | 72 | 280 | 360 | 50 | C | 5/16 | 8 | -216 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 453 | 2 | 72 | 76 | 360 | 400 | 50 | C | 5/16 | 10 | -360 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 509 | 2 | 10 | 30 | 60 | 120 | 75 | C | 5/16 | 3 | 30 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 510 | 2 | 30 | 40 | 120 | 170 | 75 | C | 5/16 | 5 | -30 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 511 | 2 | 40 | 50 | 170 | 230 | 75 | C | 5/16 | 6 | -70 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 512 | 2 | 50 | 60 | 230 | 314 | 75 | C | 5/16 | 8.4 | -190 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 513 | 2 | 60 | 68 | 314 | 400 | 75 | C | 5/16 | 10.75 | -331 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 477 | 2 | 10 | 21 | 90 | 120 | 100 | C | 5/16 | 2.727 | 62.727 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 478 | 2 | 21 | 30 | 120 | 167 | 100 | C | 5/16 | 5.222 | 10.333 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 479 | 2 | 30 | 40 | 167 | 231 | 100 | C | 5/16 | 6.4 | -25 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 480 | 2 | 40 | 50 | 231 | 326 | 100 | C | 5/16 | 9.5 | -149 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 481 | 2 | 50 | 56 | 326 | 400 | 100 | C | 5/16 | 12.333 | -290.666 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 543 | 2 | 10 | 20 | 120 | 160 | 125 | C | 5/16 | 4 | 80 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 544 | 2 | 20 | 30 | 160 | 215 | 125 | C | 5/16 | 5.5 | 50 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 545 | 2 | 30 | 40 | 215 | 290 | 125 | C | 5/16 | 7.5 | -10 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 546 | 2 | 40 | 50 | 290 | 400 | 125 | C | 5/16 | 11 | -150 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 569 | 2 | 10 | 20 | 145 | 192 | 150 | C | 5/16 | 4.7 | 98 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 570 | 2 | 20 | 30 | 192 | 250 | 150 | C | 5/16 | 5.8 | 76 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 571 | 2 | 30 | 50 | 250 | 400 | 150 | C | 5/16 | 7.5 | 25 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 586 | 2 | 20 | 42 | 232 | 400 | 175 | C | 5/16 | 7.636 | 79.272 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 35 | 43 | 50 | 80 | 25 | D |  | 3.75 | -81.25 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 43 | 52 | 80 | 120 | 25 | D |  | 4.4444 | -111.1111 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 52 | 60 | 120 | 166 | 25 | D |  | 5.75 | -179 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 60 | 72 | 166 | 200 | 25 | D |  | 2.8333 | -4 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 72 | 83 | 200 | 270 | 25 | D |  | 6.3636 | -258.1818 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 83 | 89 | 270 | 400 | 25 | D |  | 21.6667 | -1528.3333 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 454 | 2 | 24 | 40 | 50 | 107 | 50 | D | 3/8 | 3.563 | -35.5 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 455 | 2 | 40 | 62 | 107 | 220 | 50 | D | 3/8 | 5.136 | -98.454 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 456 | 2 | 62 | 71 | 220 | 280 | 50 | D | 3/8 | 6.666 | -193.333 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 457 | 2 | 71 | 83 | 280 | 400 | 50 | D | 3/8 | 10 | -430 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 514 | 2 | 10 | 40 | 55 | 130 | 75 | D | 3/8 | 2.5 | 30 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 515 | 2 | 40 | 50 | 130 | 172 | 75 | D | 3/8 | 4.2 | -38 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 516 | 2 | 50 | 60 | 172 | 240 | 75 | D | 3/8 | 6.8 | -168 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 517 | 2 | 60 | 70 | 240 | 320 | 75 | D | 3/8 | 8 | -240 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 518 | 2 | 70 | 77 | 320 | 400 | 75 | D | 3/8 | 11.429 | -480 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 482 | 2 | 10 | 30 | 80 | 135 | 100 | D | 3/8 | 2.75 | 52.5 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 483 | 2 | 30 | 40 | 135 | 190 | 100 | D | 3/8 | 5.5 | -30 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 484 | 2 | 40 | 50 | 190 | 260 | 100 | D | 3/8 | 7 | -90 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 485 | 2 | 50 | 64 | 260 | 400 | 100 | D | 3/8 | 10 | -240 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 547 | 2 | 10 | 20 | 100 | 123 | 125 | D | 3/8 | 2.3 | 77 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 548 | 2 | 20 | 30 | 123 | 170 | 125 | D | 3/8 | 4.7 | 29 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 549 | 2 | 30 | 40 | 170 | 235 | 125 | D | 3/8 | 6.5 | -25 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 550 | 2 | 40 | 50 | 235 | 328 | 125 | D | 3/8 | 9.3 | -137 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 551 | 2 | 50 | 55 | 328 | 400 | 125 | D | 3/8 | 14.4 | -392 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 572 | 2 | 10 | 20 | 140 | 180 | 150 | D | 3/8 | 4 | 100 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 573 | 2 | 20 | 30 | 180 | 228 | 150 | D | 3/8 | 4.8 | 84 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 574 | 2 | 30 | 55 | 228 | 400 | 150 | D | 3/8 | 6.88 | 21.6 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 587 | 2 | 20 | 30 | 194 | 257 | 175 | D | 3/8 | 6.3 | 68 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 588 | 2 | 30 | 47 | 257 | 400 | 175 | D | 3/8 | 8.412 | 4.647 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 36 | 54 | 50 | 105 | 25 | E |  | 3.0556 | -60 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 54 | 63 | 105 | 147 | 25 | E |  | 4.6667 | -147 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 63 | 72 | 147 | 200 | 25 | E |  | 5.8889 | -224 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 72 | 82 | 200 | 270 | 25 | E |  | 7 | -304 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 82 | 97 | 270 | 400 | 25 | E |  | 8.6667 | -440.6667 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 458 | 2 | 25 | 42 | 50 | 100 | 50 | E | 7/16 | 2.941 | -23.529 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 459 | 2 | 42 | 60 | 100 | 180 | 50 | E | 7/16 | 4.444 | -86.666 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 460 | 2 | 60 | 82 | 180 | 320 | 50 | E | 7/16 | 6.363 | -201.818 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 461 | 2 | 82 | 90 | 320 | 400 | 50 | E | 7/16 | 10 | -500 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 519 | 2 | 10 | 30 | 49 | 90 | 75 | E | 7/16 | 2.05 | 28.5 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 520 | 2 | 30 | 40 | 90 | 115 | 75 | E | 7/16 | 2.5 | 15 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 521 | 2 | 40 | 50 | 115 | 154 | 75 | E | 7/16 | 3.9 | -41 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 522 | 2 | 50 | 60 | 154 | 207 | 75 | E | 7/16 | 5.3 | -111 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 523 | 2 | 60 | 70 | 207 | 272 | 75 | E | 7/16 | 6.5 | -183 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 524 | 2 | 70 | 85 | 272 | 400 | 75 | E | 7/16 | 8.533 | -325.333 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 486 | 2 | 10 | 30 | 76 | 110 | 100 | E | 7/16 | 1.7 | 59 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 487 | 2 | 30 | 40 | 110 | 144 | 100 | E | 7/16 | 3.4 | 8 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 488 | 2 | 40 | 50 | 144 | 195 | 100 | E | 7/16 | 5.1 | -60 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 489 | 2 | 50 | 60 | 195 | 272 | 100 | E | 7/16 | 7.7 | -190 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 490 | 2 | 60 | 72 | 272 | 400 | 100 | E | 7/16 | 10.666 | -367.999 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 552 | 2 | 10 | 20 | 100 | 107 | 125 | E | 7/16 | 0.7 | 93 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 553 | 2 | 20 | 30 | 107 | 132 | 125 | E | 7/16 | 2.5 | 57 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 554 | 2 | 30 | 40 | 132 | 174 | 125 | E | 7/16 | 4.2 | 6 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 555 | 2 | 40 | 50 | 174 | 240 | 125 | E | 7/16 | 6.6 | -90 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 556 | 2 | 50 | 65 | 240 | 400 | 125 | E | 7/16 | 10.666 | -293.333 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 575 | 2 | 10 | 20 | 100 | 143 | 150 | E | 7/16 | 4.3 | 57 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 576 | 2 | 20 | 30 | 143 | 192 | 150 | E | 7/16 | 4.9 | 45 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 577 | 2 | 30 | 49 | 192 | 300 | 150 | E | 7/16 | 5.684 | 21.474 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 578 | 2 | 49 | 63 | 300 | 400 | 150 | E | 7/16 | 7.143 | -50 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 589 | 2 | 20 | 30 | 193 | 228 | 175 | E | 7/16 | 3.5 | 123 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 590 | 2 | 30 | 40 | 228 | 283 | 175 | E | 7/16 | 5.5 | 63 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 591 | 2 | 40 | 50 | 283 | 362 | 175 | E | 7/16 | 7.9 | -33 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 592 | 2 | 50 | 54 | 362 | 400 | 175 | E | 7/16 | 9.5 | -113 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 20 | 27 | 225 | 270 | 200 | E | 7/16 | 6.4286 | 96.4286 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 27 | 31.5 | 270 | 300 | 200 | E | 7/16 | 6.6667 | 90 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 31.5 | 40 | 300 | 400 | 200 | E | 7/16 | 11.7647 | -70.5882 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 37 | 52 | 50 | 80 | 25 | F |  | 2 | -24 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 52 | 63 | 80 | 120 | 25 | F |  | 3.6364 | -109.0909 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 63 | 72 | 120 | 160 | 25 | F |  | 4.4444 | -160 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 72 | 82 | 160 | 220 | 25 | F |  | 6 | -272 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 82 | 93 | 220 | 300 | 25 | F |  | 7.2727 | -376.3636 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 93 | 104 | 300 | 400 | 25 | F |  | 9.0909 | -545.4545 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 462 | 2 | 27 | 45 | 50 | 90 | 50 | F | 1/2 | 2.222 | -9.999 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 463 | 2 | 45 | 62 | 90 | 147 | 50 | F | 1/2 | 3.353 | -60.882 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 464 | 2 | 62 | 80 | 147 | 260 | 50 | F | 1/2 | 6.277 | -242.222 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 465 | 2 | 80 | 97 | 260 | 400 | 50 | F | 1/2 | 8.235 | -398.824 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 525 | 2 | 10 | 40 | 50 | 100 | 75 | F | 1/2 | 1.666 | 33.333 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 526 | 2 | 40 | 50 | 100 | 130 | 75 | F | 1/2 | 3 | -20 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 527 | 2 | 50 | 60 | 130 | 175 | 75 | F | 1/2 | 4.5 | -95 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 528 | 2 | 60 | 70 | 175 | 231 | 75 | F | 1/2 | 5.6 | -161 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 529 | 2 | 70 | 80 | 231 | 300 | 75 | F | 1/2 | 6.9 | -252 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 530 | 2 | 80 | 92 | 300 | 400 | 75 | F | 1/2 | 8.333 | -366.666 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 491 | 2 | 10 | 28 | 72 | 100 | 100 | F | 1/2 | 1.555 | 56.444 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 492 | 2 | 28 | 40 | 100 | 126 | 100 | F | 1/2 | 2.166 | 39.333 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 493 | 2 | 40 | 50 | 126 | 165 | 100 | F | 1/2 | 3.9 | -30 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 494 | 2 | 50 | 60 | 165 | 220 | 100 | F | 1/2 | 5.5 | -110 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 495 | 2 | 60 | 70 | 220 | 291 | 100 | F | 1/2 | 7.1 | -206 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 496 | 2 | 70 | 81 | 291 | 400 | 100 | F | 1/2 | 9.909 | -402.636 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 557 | 2 | 10 | 20 | 100 | 107 | 125 | F | 1/2 | 0.7 | 93 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 558 | 2 | 20 | 30 | 107 | 123 | 125 | F | 1/2 | 1.6 | 75 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 559 | 2 | 30 | 40 | 123 | 155 | 125 | F | 1/2 | 3.2 | 27 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 560 | 2 | 40 | 50 | 155 | 209 | 125 | F | 1/2 | 5.4 | -61 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 561 | 2 | 50 | 60 | 209 | 272 | 125 | F | 1/2 | 6.3 | -106 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 562 | 2 | 60 | 73 | 272 | 400 | 125 | F | 1/2 | 9.846 | -318.769 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 579 | 2 | 10 | 20 | 100 | 130 | 150 | F | 1/2 | 3 | 70 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 580 | 2 | 20 | 30 | 130 | 170 | 150 | F | 1/2 | 4 | 50 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 581 | 2 | 30 | 50 | 170 | 272 | 150 | F | 1/2 | 5.1 | 17 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 582 | 2 | 50 | 70 | 272 | 400 | 150 | F | 1/2 | 6.4 | -48 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 593 | 2 | 20 | 30 | 191 | 220 | 175 | F | 1/2 | 2.9 | 133 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 594 | 2 | 30 | 40 | 220 | 262 | 175 | F | 1/2 | 4.2 | 94 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 595 | 2 | 40 | 50 | 262 | 320 | 175 | F | 1/2 | 5.8 | 30 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 596 | 2 | 50 | 60 | 320 | 400 | 175 | F | 1/2 | 8 | -80 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 20 | 30 | 225 | 275 | 200 | F | 1/2 | 5 | 125 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 30 | 40 | 275 | 335 | 200 | F | 1/2 | 6 | 95 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 40 | 49 | 335 | 400 | 200 | F | 1/2 | 7.2222 | 46.1111 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 38 | 55 | 50 | 80 | 25 | G |  | 1.7647 | -17.0588 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 55 | 65 | 80 | 110 | 25 | G |  | 3 | -85 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 65 | 73 | 110 | 140 | 25 | G |  | 3.75 | -133.75 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 73 | 83 | 140 | 190 | 25 | G |  | 5 | -225 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 83 | 92 | 190 | 250 | 25 | G |  | 6.6667 | -363.3333 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 92 | 102 | 250 | 320 | 25 | G |  | 7 | -394 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 102 | 112 | 320 | 400 | 25 | G |  | 8 | -496 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 466 | 2 | 28 | 62 | 50 | 116 | 50 | G | 9/16 | 1.941 | -4.353 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 467 | 2 | 62 | 72 | 116 | 155 | 50 | G | 9/16 | 3.9 | -125.8 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 468 | 2 | 72 | 92 | 155 | 270 | 50 | G | 9/16 | 5.75 | -259 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 469 | 2 | 92 | 105 | 270 | 400 | 50 | G | 9/16 | 10 | -650 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 531 | 2 | 10 | 40 | 47 | 88 | 75 | G | 9/16 | 1.366 | 33.333 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 532 | 2 | 40 | 54 | 88 | 120 | 75 | G | 9/16 | 2.286 | -3.429 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 533 | 2 | 54 | 65 | 120 | 160 | 75 | G | 9/16 | 3.636 | -76.363 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 534 | 2 | 65 | 80 | 160 | 246 | 75 | G | 9/16 | 5.733 | -212.666 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 535 | 2 | 80 | 100 | 246 | 400 | 75 | G | 9/16 | 7.7 | -370 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 497 | 2 | 10 | 40 | 71 | 110 | 100 | G | 9/16 | 1.3 | 58 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 498 | 2 | 40 | 50 | 110 | 140 | 100 | G | 9/16 | 3 | -10 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 499 | 2 | 50 | 70 | 140 | 240 | 100 | G | 9/16 | 5 | -110 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 500 | 2 | 70 | 90 | 240 | 400 | 100 | G | 9/16 | 8 | -320 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 563 | 2 | 10 | 20 | 100 | 107 | 125 | G | 9/16 | 0.7 | 93 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 564 | 2 | 20 | 30 | 107 | 118 | 125 | G | 9/16 | 1.1 | 85 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 565 | 2 | 30 | 40 | 118 | 150 | 125 | G | 9/16 | 3.2 | 22 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 566 | 2 | 40 | 50 | 150 | 194 | 125 | G | 9/16 | 4.4 | -26 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 567 | 2 | 50 | 60 | 194 | 246 | 125 | G | 9/16 | 5.2 | -66 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 568 | 2 | 60 | 82 | 246 | 400 | 125 | G | 9/16 | 7 | -174 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 583 | 2 | 10 | 20 | 100 | 120 | 150 | G | 9/16 | 2 | 80 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 584 | 2 | 20 | 41 | 120 | 200 | 150 | G | 9/16 | 3.81 | 43.81 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 585 | 2 | 41 | 77 | 200 | 400 | 150 | G | 9/16 | 5.555 | -27.777 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 597 | 2 | 20 | 30 | 191 | 212 | 175 | G | 9/16 | 2.1 | 149 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 598 | 2 | 30 | 40 | 212 | 243 | 175 | G | 9/16 | 3.1 | 119 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 599 | 2 | 40 | 50 | 243 | 282 | 175 | G | 9/16 | 3.9 | 87 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 600 | 2 | 50 | 60 | 282 | 344 | 175 | G | 9/16 | 6.2 | -28 | 0 | 0 | 0 | 0 | 0 | 0
[18 empty] | 601 | 2 | 60 | 68 | 344 | 400 | 175 | G | 9/16 | 7 | -76 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 20 | 50 | 225 | 350 | 200 | G | 9/16 | 4.1667 | 141.6667 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 50 | 59 | 350 | 400 | 200 | G | 9/16 | 5.5556 | 72.2222 | 0 | 0 | 0 | 0 | 0 | 0

## PartNumberAssistant
ZW4000 Fire Valve Part Number Assistant | [17 empty] | Z3000 Fire Valve Part Number Assistant | [14 empty] | ZW4100 Fire Valve Part Number Assistant | [16 empty] | Z2100 Fire Valve Part Number Assistant
Check off the box in each group that matches the choice you want. | [17 empty] | Check off the box in each group that matches the choice you want. | [14 empty] | Check off the box in each group that matches the choice you want. | [16 empty] | Check off the box in each group that matches the choice you want.
If a choice is blank, this is standard and you add nothing to the part number. | [17 empty] | If a choice is blank, this is standard and you add nothing to the part number. | [14 empty] | If a choice is blank, this is standard and you add nothing to the part number. | [16 empty] | If a choice is blank, this is standard and you add nothing to the part number.
| If there are letters after the checkbox, then you add those letters to the part number in that order from left to right. | [17 empty] | If there are letters after the checkbox, then you add those letters to the part number in that order from left to right. | [14 empty] | If there are letters after the checkbox, then you add those letters to the part number in that order from left to right. | [16 empty] | If there are letters after the checkbox, then you add those letters to the part number in
A bonnet setting has to be part of the part number since the ZW4000 series valves are factory set and not field adjustable. | [32 empty] | A bonnet setting has to be part of the part number since the ZW4100 series valves are factory set and not field adjustable. | [18 empty] | that order from left to right.
| The flow curves must be used by the system designer to select the correct bonnet setting. | [17 empty] | The flow curves must be used by the system designer to verify the valve will function properly. | [14 empty] | The flow curves must be used by the system designer to select the correct bonnet setting. | [16 empty] | The flow curves must be used by the system designer to verify the valve will function properly.
Example | [17 empty] | Example | [14 empty] | Example | [16 empty] | Example
Sprinkler Floor Control Valve (Factory Set) | [17 empty] | 2-1/2" Sprinkler Floor Control Valve (Adjustable) | [14 empty] | 1-1/2" Sprinkler Floor Control Valve or Hose Rack Valve (Factory Set) | [16 empty] | 1-1/2" Hose Valve (Adjustable)
|  |  | Angle Body |  | Threaded Ends | [6 empty] | Rough |  | Bonnet Setting Type | [7 empty] | Angle Body |  | Threaded Ends |  | Supervisory Switch |  |  |  |  | Rough |  |  |  |  | Angle Body | Threaded Ends |  | Supervisory Switch |  |  |  |  | Rough |  | Bonnet Setting Type | [8 empty] | 1-½" National Hose Thread
[5 empty] | X |  | Monitor Switch |  |  | No Handwheel |  | Chrome |  |  | -N | -O | -P | [8 empty] | X | SS |  | No Handwheel |  | Chrome |  |  |  |  | X | X |  |  | SS |  | No Handwheel |  | Chrome |  |  | -J | -K | -L |  |  |  |  | All | X
ZW4004 |  |  | Globe Body |  | Grooved Ends |  | Adapter Bracket |  |  | Capped Bonnet |  | Plated | [5 empty] | Z3004 |  |  |  | Globe Body |  | Grooved Ends |  | Monitor Switch |  |  | Capped Bonnet |  | Plated |  | ZW4104 |  |  |  | Grooved Ends |  | Monitor Switch |  |  | Capped Bonnet |  | Plated | [5 empty] | Z2100 |  |  |  | Angle Body | Special Thread |  |  | w/Cap and Chain |  | Rough
|  |  | X | IL |  | G | X | MSA |  |  | CAP |  | CH |  | -Q | -R | -S |  |  |  |  | X | IL | X | G | Adapter Bracket |  |  |  | CAP |  | CH | [5 empty] | G | Adapter Bracket |  |  |  | CAP |  | CH | X | -M | -N | -O |  |  |  |  | NPT Threaded |  | ST |  | X | C/C | Chrome
[27 empty] | MSA | [11 empty] | X | MSA | [13 empty] | Inlet | [5 empty] | Plated
|  | In this example the part number would be ZW4004ILMSA-T | [11 empty] | X | -T | -U |  |  |  |  | In this example the part number would be Z3004ILGSS | [13 empty] | In this example the part number would be ZW4104MSA-M | [11 empty] | -P | -Q | [6 empty] | NPT Threaded Outlet |  |  |  |  | X | CH
[50 empty] | Z2105 |  |  |  | Hose Rack Valve
2-1/2" Hose Valve (Factory Set) | [17 empty] | 2-1/2" Hose Valve (Adjustable) | [14 empty] | 1-1/2" Hose Valve (Factory Set)
|  |  | Angle Body |  | Threaded Inlet |  | 2-½" National Hose Thread |  |  |  |  | Rough |  | Bonnet Setting Type | [7 empty] | Angle Body |  | Threaded Inlet |  | 2-½" National Hose Thread |  |  |  |  | Rough |  |  |  |  | Angle Body | Threaded Inlet |  | 1-½" National Hose thread |  |  |  |  | Rough |  | Bonnet Setting Type | [6 empty] | In this example the part number would be Z2100C/CCH
[12 empty] | Chrome |  |  | -N | -O | -P | [13 empty] | Chrome | [12 empty] | Chrome |  |  | -J | -K | -L
ZW4000 |  |  | Globe Body |  | Grooved Inlet |  | 3" Hose Thread |  |  | w/Cap and Chain |  | Plated | [5 empty] | Z3000 |  |  |  | Globe Body |  | Grooved Inlet |  | 3" Hose Thread |  |  | w/Cap and Chain |  | Plated |  | ZW4100 |  |  |  | Grooved Inlet |  | Special Thread |  |  | w/Cap and Chain |  | Plated | [5 empty] | 1-1/2" Hose Valve (Adjustable)
|  |  |  | IL |  | G |  | SF |  |  | CC |  | CH |  | -Q | -R | -S | [5 empty] | IL |  | G |  | SF |  |  | C/C |  | CH | [5 empty] | G |  | ST |  |  | CC |  | CH |  | -M | -N | -O | [5 empty] | 1-½" National Hose Thread
[7 empty] | Special Thread | [18 empty] | Special Thread | [27 empty] | All
[8 empty] | ST | [6 empty] | -T | -U | [10 empty] | ST | [19 empty] | -P | -Q |  | Z2100 |  |  |  | Angle Body | Special Thread |  |  | w/Cap and Chain |  | Rough
[54 empty] | NPT Threaded |  | ST |  |  | C/C | Chrome
2-1/2" Sprinkler Floor Control Valve (Factory Set) | [19 empty] | Hose Rack Valve | [10 empty] | Rough |  | 1-1/2" Sprinkler Floor Control Valve or Hose Rack Valve (Factory Set) | [20 empty] | Inlet | [5 empty] | Plated
|  |  | Angle Body |  | Threaded Ends |  | Supervisory Switch |  |  |  |  | Rough |  | Bonnet Setting Type | [7 empty] | Angle Body | [8 empty] | Chrome |  |  |  |  | Angle Body | Threaded Ends |  | Supervisory Switch |  |  |  |  | Rough |  | Bonnet Setting Type | [8 empty] | NPT Threaded Outlet | [5 empty] | CH
[8 empty] | SS |  | No Handwheel |  | Chrome |  |  | -N | -O | -P | [8 empty] | NPT Threaded Outlet |  |  |  |  | Plated | [8 empty] | SS |  | No Handwheel |  | Chrome |  |  | -J | -K | -L | Z2105 |  |  |  | Hose Rack Valve
ZW4004 |  |  | Globe Body |  | Grooved Ends |  | Monitor Switch |  |  | Capped Bonnet |  | Plated | [5 empty] | Z3005 |  |  |  | Globe Body | [9 empty] | CH | ZW4104 |  |  |  | Grooved Ends |  | Monitor Switch |  |  | Capped Bonnet |  | Plated
|  |  |  | IL |  | G | Adapter Bracket |  |  |  | CAP |  | CH |  | -Q | -R | -S | [5 empty] | IL | [14 empty] | G | Adapter Bracket |  |  |  | CAP |  | CH |  | -M | -N | -O
[8 empty] | MSA | [31 empty] | MSA | [10 empty] | Qty |  |  | Part number |  |  | Notes
|  |  | Specify if the body should be tapped and plugged for gauges. | [11 empty] | -T | -U |  | 2-1/2" Sprinkler Floor Control Valve (Adjustable) | [28 empty] | -P | -Q
[22 empty] | Angle Body |  | Threaded Ends |  | Supervisory Switch |  |  |  |  | Rough
[27 empty] | SS |  | No Handwheel |  | Chrome
| Qty |  | Part number | [5 empty] | Notes | [8 empty] | Z3004 |  |  |  | Globe Body |  | Grooved Ends |  | Monitor Switch |  |  | Capped Bonnet |  | Plated |  |  | Qty |  | Part number |  |  |  |  | Notes
[23 empty] | IL |  | G | Adapter Bracket |  |  |  | CAP |  | CH
MSA
Specify if the body should be tapped and plugged for gauges.
[19 empty] | Qty |  |  | Part number | [5 empty] | Notes

## ValveList
Qty | Floor | Stair / Standpipe | Static Inlet (psi) | Residual Inlet (psi) | Flow (gpm) | Desired Residual Outlet Min (psi) | Desired Residual Outlet Max (psi) | Valve Setting | Actual Static Outlet | Actual Residual Outlet | Model (Part Number)