Copyright 2010 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION ### - GREASE WASTE INTERCEPTORS

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

- GENERAL

      - RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

      - SUMMARY

        - Section Includes:

          - Grease interceptors.

      - DEFINITIONS

Retain definitions remaining after this Section has been edited.

        - FRP:  Fiberglass-reinforced plastic.

        - PDI: Plumbing and Drainage Institute

        - GREASE INTERCEPTOR: Elliptical fiberglass (FRP) tank system designed with built-in inlet piping and baffle penetration that introduces wastewater in a tangential laminar flow to reduce disruption of collected grease and solids. Tank system is designed to capture and hold grease and solids to maximize waste retention and optimize Stokes Law separation. System backed by 30 year manufacturer warranty.

          - GRAVITY GREASE INTERCEPTOR: Elliptical fiberglass (FRP) interceptor that is certified to meet IAPMO/ANSI Z1001-2007 and applicable sections of the latest editions of the Uniform Plumbing Code or the International Plumbing Code. Interceptor is designed to deliver 100 PPM non-emulsified free-floating oil and grease and 350 PPM Total Suspended Solids effluent quality based on inlet peak fixture flow.

          - HYDROMECAHNICAL OR PDI CERTIFIED GREASE INTERCEPTOR: Elliptical fiberglass (FRP) interceptor that is certified to meet PDI G-101 Standard rated up to 100 GPM flow.

          - CSA CERTIFIED GREASE INTERCEPTOR: Elliptical fiberglass (FRP) interceptor that is certified to meet CSA B481 Standard rated at either 50 GPM or 100 GPM flow.

      - ACTION SUBMITTALS

        - Product Data:    Include materials of fabrication, dimensions, rated capacities, retention capacities, operating characteristics, size and location of each pipe connection, furnished specialties, and accessories.

        - Shop Drawings:  For each type and size of interceptor indicated.

- 1. 	Include materials of construction, dimensions, rated capacities, retention capacities, location and size of each pipe connection, furnished specialties, and accessories.

      - INFORMATIONAL SUBMITTALS

        - Coordination Drawings:  Interceptors, drawn to scale, on which the following items are shown and coordinated with each other, based on input from Installers of the items involved:

          - Grease Interceptors.

          - Piping connections.  Include size, location, and elevation of each.

          - Interface with underground structures and utility services.

      - PROJECT CONDITIONS

Retain this article if interruption of existing sanitary or storm sewer service is required.

        - Interruption of Existing Sewer Services:  Do not interrupt services to facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary sewer services according to requirements indicated:

          - Notify [Architect] [Construction Manager] [Owner] no fewer than [seven] <Insert number> days in advance of proposed interruption of service.

          - Do not proceed with interruption of sewer services without [Architect's] [Construction Manager's] [Owner's] written permission.

- PRODUCTS

      - GREASE  INTERCEPTORS

Indicate on Drawings the number, size, and arrangement of compartments and baffles in oil interceptors in first paragraph below.  Delete optional text below and insert name of authority having jurisdiction for interceptors complying with requirements of authorities having jurisdiction.  See Editing Instruction No. 3 in the Evaluations.

        - Basis of Design:  Elliptical Fiberglass (FRP) grease interceptor construction, as supplied by Green Turtle Americas Ltd. or Green Turtle Technologies Ltd., with inlet piping and baffle penetration designed to introduce wastewater in a tangential laminar flow pattern, to be appropriately sized based on anticipated usage and flow rates to meet applicable sanitary sewer discharge limits, incl. municipal by-laws.

          - Include accessways, tanks, and piping and baffle openings to retain grease and solids and to permit tangential laminar wastewater flow.

          - Factory installed Schedule 40 PVC cement welded type socket ports, or straight pipe, fitted into interceptor walls for each pipe connection.

First subparagraph below is optional.

          - Accessway Extension Collar:

            - Fiberglass risers (EC2), 24-inch (610-mm). 36-inch (915-mm) optional alternate.

          - Accessway Frames and Covers:     Round cover with non slip cover finish, gasketed and non vented top design with “Proceptor” lettering cast into cover.

            - Cast Iron:   AASHTO M306 Traffic load rated.  24 inch- (610-mm-) diameter cover with 0.25” (6-mm-) gasket.  Two closed pickholes.  Non Bolted or Bolted option.  Weight 249 lbs. ASTM A48 CL35B. 36-inch (915-mm) optional alternate is acceptable to match fiberglass risers.

            - Fiberglass:  Pedestrian loading 24” diameter bolted and gasketed.

          - Watertight Flexible Caulking: Sikaflex 255 or Sikaflex 221 or approved alternate to provide watertight seal at extension collar joints.

If more than one grease interceptor is required, delete paragraph below and schedule grease interceptors on Drawings.

        - Capacities and Characteristics:

          - Number of Compartments: <x cells>

          - Grease Retention Capacity: <xxx USG>

          - Solids Retention Capacity:  <xxx USG >

          - Inlet and Outlet Schedule 40 PVC Pipe Size:  <4”/6”>

            - Centerline of Inlet to Floor:  <Insert inches (mm)>.

            - Centerline of Outlet to Floor:  <Insert inches (mm)>.

          - Vent Pipe Size:  <3”>.

          - Installation Position:   Above grade or Underground with accessway collar riser to grade.

          - OPTIONS as required:

            - 4” Side or Top Suction port for remote pump-out.

            - Alarm for high oil accumulation.  Includes alarm probe to be installed in top of tank accessway and alarm panel for indoor wall mount.

          - Green Turtle Proceptor Model:  :  <GMC XXX>.

Coordinate two "Oil Interceptors" paragraphs below with Section 231113 "Facility Fuel-Oil Piping" for waste-oil storage tanks and oil and vent piping.

      - FIBERGLASS ACCESSWAY RISERS

Retain this article for manhole risers for underground concrete interceptors to provide access from grade level to interior of interceptors.

        - Fiberglass accessway extensions:  Fiberglass wound pipe.

          - Length:  From top of underground tank to underside of access frame at grade.

          - Extension Sections:  0.25-inch (6-mm) minimum thickness and [24-inch (610-mm) or 36-inch (915-mm) I.D.] as a single continuous piece, without joints unless approved by the manufacturer.

            - Sealant:  Watertight Flexible Caulking, Sikaflex 255 or Sikaflex 221 or approved alternate to provide watertight seal at extension collar joining to tank on bottom  and access frame at top.

- EXECUTION

      - EARTHWORK

        - Excavating, trenching, and backfilling are specified in Section ### "Earth Moving."

      - INSTALLATION

        - Install fiberglass interceptors according to manufacturer’s installation instructions.

      - CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

        - Piping installation requirements are specified in Section ### "Sanitary Waste and Vent Piping." Drawings indicate general arrangement of piping, fittings, and specialties.

        - Make piping connections between interceptors and piping systems.

      - IDENTIFICATION

        - Identification materials and installation are specified in Section ### "Earth Moving." Arrange for installation of green warning tapes directly over piping and at outside edges of underground interceptors.

          - Use warning tapes or detectable warning tape over ferrous piping.

          - Use detectable warning tape over nonferrous piping and over edges of underground structures.

END OF SECTION ###